## Arhitectural solutions
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03273 Repair and modernization of the “Ion Creangă” Theoretical Lyceum from Fălești town (First phase)
1 | Suspended ceilings made of prefabricated panels including grid system with physical and visual characteristics type Rockfon Artic E24 with partially visible structure and dimensions 600 x 600 x 15mm, class 1/C/0N according to EN 13964
2 | Plastic floors mounted on the existing substrate, cleaned, including PVC sills, in rooms with areas greater than 16 sqm, with PVC carpet glued with pre-bonded / Omogenius PVC carpet, thickness = 2-2,3 mm; change:PVC profile, PVC sill in PVC PVC connection profile R=30 mm - 0,6 m/m2. Color according to the design.
3 | Interior partitions made of aluminum profiles with mat sandwich filling composed of PU boards and 1 mm sheet metal on both sides. The windows will be made of 4+4 mm transparent triplex glass. Doors will be equipped with stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); C-3 7500x2150(h)
4 | Interior wooden doors in a can, with 2 mm metal frame, color RAL 7014 and 44 mm plywood laminated wood plywood canvas, color RAL 1014 with mat varnish. With 1 mm stainless steel protection plate at the bottom and 4+4 mm transparent triplex glass 4+4 mm and stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); UI-1 1150x2020(h)

## Water
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03273 Repair and modernization of the “Ion Creangă” Theoretical Lyceum from Fălești town (First phase)
1 | Public washbasin (lavatory) made of semi-porcelain / sanitary porcelain, mounted on pedestal, with PP siphon
| Product type | Washbasin for public sanitary facilities
| Installation type | Wall-mounted basin with full pedestal
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, hygienic, stain-resistant glaze
| Mounting method | Wall-fixed with anchor bolts; pedestal for aesthetic and pipe concealment
| Pedestal type | Full pedestal (ceramic), matching basin
| Basin dimensions (approx.) | 550–600 mm (W) × 450–500 mm (D)
| Height (installed) | Approx. 800–850 mm from finished floor level
| Tap hole | Single hole Ø35 mm (standard)
| Overflow | Integrated overflow system
| Waste outlet diameter | Ø45 mm
| Siphon | Bottle trap, polypropylene (PP), Ø32 mm
| Water supply connection | ½" flexible connectors
| Fixing kit | Included (bolts, plugs, caps)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 14688 (washbasins)
| Application | Public buildings, offices, schools, commercial premises
2 | Chrome-Plated Mixer Tap with Swivel Spout (Public Toilets)
| Product type | Basin mixer tap for public sanitary facilities
| Installation type | Deck-mounted (single-hole installation)
| Body material | Brass (CuZn), chrome-plated finish
| Surface finish | Polished chrome, corrosion-resistant
| Spout type | Swivel (pivoting) spout
| Spout reach | Approx. 150–200 mm
| Cartridge type | Ceramic cartridge, 35–40 mm
| Control type | Single-lever mixer
| Water supply connection | Flexible hoses ½"
| Aerator | Anti-limescale aerator, M24/M22
| Flow rate | 5–9 L/min (depending on pressure)
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Water temperature range | 5°C – 90°C
| Fixing system | Mounting kit included (gasket, fixing nut, bolts)
| Application | Public toilets, schools, offices, commercial buildings
| Compliance | EN 817 (mechanical mixer taps)

## HAVC
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03273 Repair and modernization of the “Ion Creangă” Theoretical Lyceum from Fălești town (First phase)
1 | Steel Panel Radiator Type “Kermi Profil-K" 22K 500×1000 or equivalent
| Product type | Steel panel radiator
| Model | Type 22K (two panels + two convectors)
| Dimensions (H × L) | 500 × 1000 mm
| Depth | Approx. 100 mm
| Material | Cold-rolled steel panels
| Surface finish | Powder-coated, white (RAL 9016 standard)
| Heat output (90/70/20°C) | Approx. 1850 W
| Heat output (75/65/20°C) | Approx. 1450 W
| Maximum operating temperature | 110°C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Water content | Approx. 5–6 liters
| Weight | Approx. 25–26 kg
| Connections | 4 × G 1/2" female threaded (side connections)
| Installation type | Wall-mounted (brackets included)
| Air vent & plug | Included
| Standard compliance | EN 442
2 | steel panel radiator “Kermi Profil-K" Type 33K 500×1100 or equivalent
| Product type | Steel panel radiator
| Model | Type 33K (three panels + three convectors)
| Dimensions (H × L × D) | 500 × 1100 × ~155 mm
| Material | Cold-rolled steel panel construction
| Surface finish | Powder-coated white (standard RAL, corrosion-protected)
| Heat output (90/70/20 °C) | ~2914 W
| Heat output (75/65/20 °C) | ~2287 W
| Water content | ~8.36 L
| Weight | ~50.5 kg
| Maximum operating temperature | 110 °C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Connections | 4 × G 1/2″ internal threads
| Connecting pitch | H – 54 mm
| Installation type | Wall-mounted radiator
| Compliance | EN 442 (European radiator standard)
3 | Danfoss Thermostatic Radiator Valve with Pre-Setting RA-N, DN 15 or equivalent
| Product type | Thermostatic radiator valve with pre-setting
| Model | RA-N
| Nominal diameter | DN 15 (≈ 1/2″)
| Connection type | Rp 1/2″ internal thread
| Valve configuration | Normal flow type (presetting on the radiator inlet)
| Body material | Brass with corrosion-resistant surface finish
| Presetting | Integrated presetting ring with adjustable Kv steps
| Kv range | Approx. 0.04 – 0.7 m³/h (depending on presetting position)
| Kv at presetting “N” | Approx. 0.73 m³/h
| Max. operating temperature | Up to 120 °C
| Max. working pressure | 10 bar
| Test pressure | 16 bar
| Seal material | EPDM or equivalent elastomer
| Differential pressure tolerance | Up to ~0.6 bar for stable control
| Surface finish | Nickel-plated or chrome plated (depending on manufacturer)
| Standards compliance | EN 215 (Thermostatic radiator valves)
| Accessories | Compatible with thermostatic heads (RA, RAS series or equivalent)
| Country of manufacture | Denmark (Danfoss)
4 | Danfoss Radiator Shut-off Valve (RLV), DN 15 or equivalent
| Product type | Radiator shut-off / lockshield valve
| Model | RLV, DN 15
| Connection size | R 1/2″ (internal thread) – radiator and system connections
| Design | Straight lockshield valve
| Body material | Brass with nickel-plated finish (corrosion-resistant)
| Maximum operating temperature | 120 °C
| Maximum working pressure | 10 bar
| Test pressure | 16 bar
| Kv (flow coefficient) | Approx. 2.20–2.50 m³/h
| Seal material | EPDM or equivalent
| Surface finish | Nickel plated
| Thread standard | ISO 7/1 (R 1/2″)
| Type variants | Straight or angled, standard or self-sealing tailpiece
| Country of manufacture | Denmark (Danfoss)
5 | Thermostatic Element Danfoss RA 2991 or equivalent
| Model / Part No. | RTR 7090 / 013G7090
| Type | Thermostatic radiator thermostat element
| Application | For automatic temperature control of radiator valves
| Compatibility | Designed for RTR series radiator valves (e.g., RTR-N, RTR-G), can be combined with appropriate radiator valve bodies
| Sensing element | Gas-filled bulb sensor
| Mounting / Connection | Clip-on type (quick clip fitting to valve)
| Adjustment range (room air temperature) | 5 °C to 26 °C
| Temperature range, operational | Min. 5 °C – Max. 26 °C setpoint range
| Colour | White
| Max. permitted system temperature | Approx. 120 °C (typical TRV rating for paired valves)
| Max. working pressure | Approx. 10 bar (based on typical radiator thermostatic valve ratings)
| Ratio / Sensitivity | Proportional direct-acting thermostat with small proportional band
| Housing material | Plastic body with internal sensing element
| Warranty | Approx. 1 year
| Country of manufacture | Denmark (Danfoss)
| Standards compliance | EN 215 (when combined with compliant radiator valve)
6 | Fiart PP-R Pipe Ø20 mm or equivalent
| Material | Polypropylene Random Copolymer (PP-R, Type 3)
| Standard | EN ISO 15874; DIN 8077/8078
| Application | Hot and cold water supply, potable water, HVAC systems
| Manufacturing method | Extrusion
| Joining method | Socket fusion welding (polyfusion)
| Outside diameter | 20 mm
| Wall thickness | 3.4 mm (PN20 typical)
| Inside diameter | ~13.2 mm
| Pressure class | PN20 (20 bar at 20°C)
| Working temperature | 0°C to +70°C (continuous)
| Max. temperature | Up to 90–95°C (short-term)
| Density | ~0.9 g/cm³
| Thermal conductivity | ~0.21 W/m·K
| Linear expansion coefficient | ~0.15 mm/m·K
| Surface | Smooth inner surface, low hydraulic resistance
| Corrosion resistance | Resistant to corrosion and scaling
| Chemical resistance | Resistant to acids, alkalis, salts
| Hygiene | Non-toxic, suitable for drinking water
| Service life | Minimum 50 years (under normal conditions)
| Installation temperature | Welding at approx. 260–270°C
| Color | Green / white / grey (manufacturer dependent)
| Marking | Manufacturer, Ø20, PN20, standard EN ISO 15874
| Compatibility | Compatible with PP-R fittings and metal inserts
7 | Clivet 2800 AqX5, ventilation / air handling unit (AHU) with heat recovery or equivalent
| Product | Air handling unit Clivet 2800 AqX5 (or equivalent)
| Type | Compact ventilation unit with heat recovery
| Application | Commercial and residential ventilation (schools)
| Installation | Indoor (Multi-V) or rooftop (Multi-N variants)
| Airflow capacity | Approx. 3000 m³/h
| Heat recovery type | Counterflow heat exchanger
| Heat recovery efficiency | Up to 90%
| Fans | EC fans with backward-curved blades
| Filtration | Supply/exhaust filters (G4, M5, F7 options)
| Heating options | Electric heater or water coil (optional)
| Cooling options | Direct expansion (DX) or water cooling (optional)
| Bypass | Integrated bypass damper (optional)
| Control | Integrated automation system (plug & play)
| Casing | Double-skin, thermally insulated (class T2)
| Noise level | Low noise operation (optimized fans)
| Energy efficiency | High efficiency, low power consumption
| Additional features | Recirculation, dampers, automation options
| Service access | Front access panels for maintenance
| Application range | Ventilation, heating, cooling in one unit
8 | Duct Fan VKMts 200
| Product | Circular inline centrifugal duct fan VKMts 200 (or equivalent)
| Type | Inline centrifugal fan for round ducts
| Application | Supply and exhaust ventilation systems
| Duct diameter | 200 mm
| Airflow capacity | Up to ~1000 m³/h
| Pressure | Medium pressure (centrifugal fan)
| Power supply | 220–240 V / 50 Hz
| Power consumption | ~140–160 W
| Current | ~0.6–0.7 A
| Motor type | Single-phase AC motor with external rotor
| Impeller | Centrifugal, backward-curved blades
| Rotation speed | ~2700–2800 rpm
| Noise level | ~50 dB(A)
| Casing material | Galvanized steel
| Protection rating | IPX4 / IP44
| Air temperature range | -25°C to +50°C
| Installation | Any position (horizontal or vertical)
| Speed control | Thyristor or transformer controller
| Motor protection | Built-in thermal protection
| Service life | Up to ~40,000 hours
| Weight | ~5–6 kg
9 | Split Air Conditioner PUHZ-ZRP71VHA
| Product | Split air conditioner PUHZ-ZRP71VHA (or equivalent)
| Series | Smart Inverter R32
| Type | Wall-mounted split system
| Compressor type | Inverter
| Cooling capacity | ~5.2 kW (18000 BTU)
| Heating capacity | ~5.6 kW
| Recommended area | Up to ~50 m²
| Power consumption (cooling) | ~1.5–1.6 kW
| Power consumption (heating) | ~1.4–1.5 kW
| Energy efficiency class | A++ / up to A+++
| Refrigerant | R32
| Airflow rate | Up to ~850 m³/h
| Noise level (indoor) | ~41–44 dB
| Noise level (outdoor) | ~56 dB
| Operating mode | Cooling / Heating
| Heating operation range | Down to -22…-25°C
| Cooling operation range | -15°C to +43°C
| Wi-Fi control | Yes (built-in)
| Air filtration | Multi-stage filtration (dust + antibacterial)
| Functions | Auto-restart, self-diagnosis, defrost, “I Feel”, 8°C heating
| Pipe connection | 1/4" – 1/2"
| Max pipe length | ~20 m
| Max height difference | ~10 m
| Indoor unit dimensions | ~970×300×224 mm
| Outdoor unit dimensions | ~802×350×555 mm
| Power supply | 220–240 V / 50 Hz
| Warranty | Typically 24 months

## Electrical
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03273 Repair and modernization of the “Ion Creangă” Theoretical Lyceum from Fălești town (First phase)
1 | Recessed LED Panel, 600×600 mm, 35 W, 4000 K
| Product type | Recessed LED ceiling luminaire (LED panel)
| Model / Format | 600 × 600 mm (suitable for 600×600 mm ceiling grid)
| Rated power | 35 W
| Light source | Integrated LED modules
| Color temperature | 4000 K (neutral white)
| Rated luminous flux | ≈ 3000–3500 lm (typical from a 35 W panel)
| Efficacy | ≈ 85–100 lm/W (dependent on manufacturer)
| CRI (Color Rendering Index) | ≥ 80 (≥ Ra80)
| Beam angle | ≈ 120° (wide uniform distribution)
| Driver type | External / integrated LED driver (electronic)
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut, manufacturer dependent)
| Housing material | Aluminium frame + steel back housing
| Diffuser / Optics | Opal / microprismatic diffuser for uniform glare-free light
| Mounting type | Recessed into suspended ceiling grid (T-bar)
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistance)
| Operating temperature | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80 B10)
| Certifications | CE
| Finish / Color | White frame (powder coated)
2 | Linear LED Light, 1200 mm, 45 W, 4000 K
| Product type | Linear LED luminaire
| Length | 1200 mm
| Rated power | 45 W
| Light source | Integrated LED
| Color temperature | 4000 K (neutral white)
| Luminous flux | ≈ 3900–4500 lm (typical from a 45 W LED)
| Efficacy | ≈ 85–100 lm/W (dependent on model)
| Color rendering (CRI) | ≥ 80 (≥ Ra80)
| Beam angle | 120° (wide light distribution)
| Driver type | Built-in / external electronic LED driver
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut – model dependent)
| Housing material | Aluminium body with steel end caps
| Diffuser | Opal or prismatic polycarbonate for uniform light
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistant)
| Operating ambient temp | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80)
| Finish / Color | White (standard)
| Certifications | CE, RoHS, EMC
| Application | Offices, corridors, retail, education, industrial interiors
3 | Illuminated Direction Indicator with Battery
| Product type | Illuminated directional indicator / emergency exit arrow sign
| Rated LED power | 3 W
| Light source | High-efficiency LEDs
| Illumination color | Green (standard for emergency direction signs)
| Symbol / Arrow type | Directional arrow or pictogram (configurable: left / right / up / down)
| Supply voltage | 220–240 V AC, 50 Hz (primary mains)
| Backup power | Rechargeable battery (internal)
| Battery type | Sealed lead-acid (SLA) or NiMH (model dependent)
| Battery autonomy | ≥ 3 hours (in emergency mode)
| Charge time | ≤ 24 hours to full charge
| LED lifetime | ≥ 50,000 h
| Viewing distance | ≥ 20–25 m (depending on size and installation)
| Ingress protection | IP20 (indoor), optional higher rating on request
| Mounting | Wall or ceiling (surface mounted)
| Housing material | ABS / polycarbonate flame-retardant enclosure
| Operating temperature | 0 °C to +40 °C (typical)
| Emergency testing | Built-in test button (optional)
| Standards / Compliance | Compliant with EN 50172 / EN 1838 (emergency lighting)
| Indicators | Charge / test LED indicators
| Finish / Color | White housing (standard)
4 | Distribution Board, 36 Modules (Flush-Mounted)
| Product type | Electrical distribution board (consumer unit)
| Model / Type | Flush-mounted distribution board, 36 modules (ЩРв-36 or equivalent)
| Installation type | Recessed / flush-mounted (in-wall installation)
| Number of modules | 36 DIN modules (3 rows × 12 modules typical)
| Rated voltage | 230/400 V AC, 50 Hz
| Rated current | Up to 63–100 A (depending on manufacturer)
| Protection class | IP30–IP40 (indoor use)
| Impact resistance | IK07 (typical)
| Material | Metal enclosure with powder coating or high-quality ABS (model dependent)
| Door type | Solid or transparent hinged door
| Mounting rail | Standard 35 mm DIN rail
| Neutral busbar (N) | Included
| Protective earth busbar (PE) | Included
| Terminal type | Screw terminals
| Cable entry | Top and bottom knockouts
| Operating temperature | –5 °C to +40 °C
| Color | White (RAL 9016 typical)
| Standards / Compliance | IEC 61439-1 / IEC 61439-3, CE
5 | Residual Current Circuit Breaker with Overcurrent Protection (RCBO), 2P, C16A, 10 mA, 6 kA
| Product type | RCBO (Residual Current Circuit Breaker with Overcurrent protection)
| Number of poles | 2P (Phase + Neutral)
| Rated current (In) | 16 A
| Tripping characteristic | Type C (magnetic curve C)
| Rated residual current (IΔn) | 10 mA
| Breaking capacity | 6 kA
| Rated voltage (Ue) | 230 V AC
| Frequency | 50/60 Hz
| Residual current type | Type AC or Type A (model dependent)
| Mounting | 35 mm DIN rail
| Protection degree | IP20 (installed in enclosure)
| Mechanical endurance | ≥ 10,000 operations
| Electrical endurance | ≥ 4,000 operations
| Terminal type | Screw clamp terminals
| Standards | IEC 61009-1
6 | Uninterruptible Power Supply (UPS), 4 kVA
| Product type | Uninterruptible Power Supply (UPS)
| Rated power capacity | 4 kVA
| Active power (typical) | 3.2–3.6 kW (depending on power factor 0.8–0.9)
| UPS topology | Online double-conversion / Line-interactive (model dependent)
| Input voltage | 220–240 V AC
| Input frequency | 50/60 Hz (auto sensing)
| Output voltage | 230 V AC ±1–2%
| Output frequency | 50/60 Hz ±0.1 Hz (online type)
| Waveform | Pure sine wave
| Transfer time | 0 ms (online) / 2–10 ms (line-interactive)
| Battery type | Sealed lead-acid (VRLA) or external battery pack
| Battery autonomy | 5–15 minutes at full load (extendable with external batteries)
| Recharge time | 4–8 hours to 90% capacity
| Bypass | Automatic and manual bypass (model dependent)
| Efficiency | ≥ 90% (online), ≥ 95% (eco mode)
| Protection features | Overload, short-circuit, battery deep discharge, overtemperature
| Communication ports | USB / RS-232 / SNMP (optional network card)
| Display | LCD display with load and battery status
| Cooling | Forced air cooling (internal fans)
| Installation type | Tower or Rack-mount (model dependent)
| Protection class | IP20 (indoor use)
| Operating temperature | 0 °C to +40 °C
| Standards / Compliance | IEC 62040-1, IEC 62040-2, CE

## Low voltage
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03273 Repair and modernization of the “Ion Creangă” Theoretical Lyceum from Fălești town (First phase)
1 | Network Video Recorder DS-8632NXI-I8/S MP/32-ch@1080p, 2 HDMI, 2 VGA, 8K or dual 4K video outputs,
| Product | 32-channel AcuSense Network Video Recorder (NVR) DS-8632NXI-I8/S
| Type | Professional IP NVR (2U chassis)
| Video inputs | Up to 32 IP cameras
| Max recording resolution | Up to 32 MP (IP cameras)
| Video compression | H.265+/H.265/H.264+/H.264
| Incoming bandwidth | Up to 320 Mbps
| Outgoing bandwidth | Up to 256 Mbps
| Decoding capability | Up to 32-ch @1080p
| HDMI output | Up to 4K (3840×2160)
| VGA output | Up to 1920×1080
| Audio | 2-ch audio out, 1-ch two-way audio
| AI analytics | AcuSense (deep learning: human/vehicle detection)
| Facial recognition | Up to 4-ch video / 8-ch image
| Perimeter protection | Up to 4 channels
| ANPR support | Yes (via cameras)
| Storage | 8 × SATA HDD bays
| Max HDD capacity | Up to 16 TB per disk
| RAID support | RAID 0/1/5/6/10
| eSATA | 1 port
| USB ports | 2 × USB 2.0 (front), 2 × USB 3.0 (rear)
| Network interface | 1 × RJ-45 Gigabit Ethernet
| Remote users | Up to 128 connections
| Protocols | TCP/IP, ONVIF, RTSP, HTTPS, etc.
| Alarm I/O | 16 in / 9 out
| Power supply | 100–240 VAC, 50/60 Hz
| Power consumption | ≤30 W (without HDD)
| Operating temperature | -10°C to +55°C
| Dimensions | 440 × 457 × 94 mm
| Weight | ≤7.1 kg (without HDD)
| Certifications | CE, CB, WEEE, UKCA
2 | Hikvision DS‑2CD1067G2‑LUF (a 6 MP outdoor/indoor fixed network camera with built-in mic and audio support
| Product type | Fixed network (IP) dome camera
| Image sensor | 1/2.7″ Progressive CMOS
| Resolution | 6 MP (3072 × 2048)
| Lens | Fixed 2.8 mm (wide) / optional 4 mm variants
| Field of View (approx.) | 102° (H) × 55° (V) × 124° (D)
| Min. Illumination | 0.01 lux @ (F1.2, AGC ON)
| Day/Night | IR cut filter with auto switch
| IR Range | Up to 10–15 m (model dependent)
| Video Compression | H.265 / H.264 / MJPEG
| Max. Frame Rate | 6 MP @ 20 fps
| Video Streaming | 3 concurrent streams
| WDR | Digital WDR (Wide Dynamic Range)
| BLC / HLC | Yes (Backlight / Highlight compensation)
| Noise Reduction | 3D Digital Noise Reduction (3D DNR)
| Audio | Built-in microphone
| Network | 1 × RJ45 10/100 Mbps
| PoE | 802.3af PoE (power over Ethernet)
| Storage | MicroSD/SDHC/SDXC card slot (up to 256 GB)
| Smart features | Motion detection, region of interest, privacy mask
| ONVIF | Profiles S/G compatible
| Power | PoE or 12 V DC
| Operating Temp. | –30 °C to +60 °C
| Ingress Protection | IP67 (dust & water resistant)
| IK Rating | IK10 (impact resistant)
| Housing material | Metal / plastic weatherproof casing
| Dimensions | Approx. Ø109 × 78 mm
| Weight | ~0.4 kg
3 | Hikvision DS-2CD1147G2H-LIU(F), a 4 MP network camera with built-in IR and advanced features
| Product type | Network (IP) turret camera
| Image sensor | 1/3″ Progressive Scan CMOS
| Effective pixels | 4 MP (2688 × 1520)
| Lens | 2.8 mm fixed lens (horizontal FOV ~102°)
| Maximum resolution | 2688 × 1520
| Min. illumination | 0.005 lux @ (F1.6, AGC ON)
| Day/Night | True D/N with mechanical IR cut filter
| IR illumination | Up to 30 m range (built-in IR LEDs)
| Video compression | H.265 / H.264 / MJPEG
| Max. frame rate | 4 MP @ 30 fps
| Video streams | 3 independent streams
| Wide Dynamic Range | Digital WDR (120 dB)
| Noise reduction | 3D DNR (Digital Noise Reduction)
| ROI / BLC / HLC | Yes (Region of Interest / Backlight / Highlight Comp)
| Audio | Built-in microphone
| Smart features | Motion detection, line crossing, intrusion detection (model dependent)
| Network | 1 × RJ45 10/100 Mbps
| Power | PoE (802.3af) or 12 V DC
| Power consumption | < 6 W typically
| On-board storage | MicroSD/SDHC/SDXC up to 256 GB
| Operating temp. | –30 °C to +60 °C
| Ingress protection | IP67 weatherproof
| Impact protection | IK10 vandal resistant
| Housing material | Metal base with plastic/metal dome
| Dimensions | Approx. Ø110 × 93 mm
| Weight | ~0.5 kg
4 | Fiber Optic Patch Panel FOBX24-1U-8LCUD03
| Product | Fiber optic patch panel FOBX24-1U-8LCUD03 (or equivalent)
| Type | Rack-mounted fiber optic distribution panel
| Form factor | 19” rack, 1U height
| Application | Fiber optic signal distribution and termination in telecom and LAN systems
| Fiber type | Multimode OM3 (50/125 µm)
| Connector type | LC Duplex
| Number of adapters | 8 × LC duplex (installed)
| Max capacity | Up to 24 LC ports (modular panel)
| Included components | LC pigtails, splice tray, heat shrink sleeves (KDSZ)
| Splice tray | 1 cassette (capacity up to 32 splices)
| Mounting type | Rack-mounted (fixed)
| Material | Metal корпус (steel), powder-coated
| Color | Grey (RAL 7035)
| Protection rating | IP22
| Impact resistance | IK07
| Dimensions (W×D×H) | 405 × 212 × 40 mm
| Weight | ~2.5–2.7 kg
| Cable management | Internal fiber routing and фиксация кабеля
| Installation accessories | Mounting brackets, screws, cable ties included
| Operating environment | Indoor installation
| Function | Splicing, termination, and patching of fiber optic cables
5 | Cloud Core Router CCR1016-12S-1S+
| Product | Cloud Core Router CCR1016-12S-1S+
| Type | Carrier-grade router / 1U rackmount
| Architecture | TILE
| CPU | Tilera TLR4-01680
| CPU cores | 16 cores
| CPU frequency | 1.2 GHz
| RAM | 2 GB
| Storage | 128 MB NAND
| Operating system | RouterOS (Level 6 license)
| Throughput | Up to ~20 Gbps (fast path)
| Ethernet / Fiber ports | 12 × SFP (1G), 1 × SFP+ (10G)
| Additional ports | 1 × USB, 1 × RJ45 serial console
| Memory expansion | microSD slot
| Display | Integrated LCD touchscreen
| Power supply | Dual redundant AC (100–240 V)
| Power consumption | Up to ~47.5 W
| Cooling | Active cooling (2 fans)
| Dimensions | 443 × 197 × 44 mm (1U rack)
| Operating temperature | -20°C to +60°C
| Protection rating | IP20
| MTBF | ~200,000 hours
| Certifications | CE, EAC, RoHS
| Included accessories | Rack ears, power cables, RJ45 SFP module
6 | Industrial PoE Switch TSX-U-2GX/SFP-24GTP-R
| Product | Industrial unmanaged PoE switch TSX-U-2GX/SFP-24GTP-R
| Manufacturer | EKF
| Type | Layer 2 unmanaged Ethernet switch
| Application | Industrial networks, CCTV, structured cabling
| Total ports | 26 ports
| RJ45 ports | 24 × 10/100/1000Base-T (Gigabit Ethernet)
| PoE support | Yes, 24 ports with PoE (up to 30 W per port)
| Uplink ports | 2 × SFP (1 Gbps)
| Switching capacity | ~52 Gbps
| MAC address table | Auto-learning, auto-aging
| Management | Unmanaged (plug & play)
| Installation | 19” rack mounting (1U)
| Power supply | 100–240 VAC
| Power per PoE port | Up to 30 W
| Housing material | Metal (industrial grade)
| Dimensions | ~440 × 280 × 44 mm
| Operating temperature | Approx. -10°C to +50°C
| Cooling | Passive / active (depending on version)
| Protection | Industrial design for stable operation
| Function | Data switching + PoE power supply
| Use cases | IP cameras, access points, VoIP, industrial LAN
7 | SFP Optical Transceiver TSX-SFP-HS2D-13-20
| Product | SFP optical transceiver TSX-SFP-HS2D-13-20 (or equivalent)
| Type | SFP (Small Form-factor Pluggable) optical module
| Application | Fiber optic data transmission (LAN, telecom, CCTV networks)
| Data rate | 2.5 Gbps
| Standards | STM-8 / OC-24 / Gigabit Ethernet
| Fiber type | Single-mode (SM)
| Transmission distance | Up to 20 km
| Wavelength | 1310 nm
| Connector type | Duplex (2 fibers)
| Form factor | SFP hot-pluggable module
| Power supply | 3.3 V
| Housing material | Metal корпус
| Mounting | Plug-in (latch mechanism)
| Dimensions | ~9 × 14 × 56 mm
| Weight | ~0.03 kg
| Series | PROxima
| Function | Optical signal transmission and reception
8 | EKF SW900PRO-EBBRT-78 Battery Pack
| Product | External battery pack SW900PRO-EBBRT-78 (or equivalent)
| Type | External battery module for UPS
| Application | Extending backup time of UPS systems
| Compatible UPS | E-Power SW900Pro-RT / RTB (3000 VA class)
| Battery type | Sealed lead-acid (VRLA)
| Number of batteries | 8 pcs
| Battery capacity | 7 Ah each
| Battery voltage | 12 V per battery
| Total system voltage | 96 V DC
| Mounting | Rackmount / standalone (1U/2U form factor)
| Dimensions (W×D×H) | ~440 × 465 × 88 mm
| Weight | ~15–21.8 kg (depending on config)
| Housing | Metal корпус
| Cooling | Passive
| Protection rating | IP20
| Function | Provides extended autonomy time for UPS
| Series | E-Power SW900Pro
9 | Wireless Access Point RBwAPG-5HacT2HnD
| Product | Outdoor wireless access point RBwAPG-5HacT2HnD (wAP ac)
| Type | Dual-band wireless access point (outdoor/indoor)
| Wi-Fi standards | 802.11a/b/g/n/ac
| Frequency bands | 2.4 GHz and 5 GHz (simultaneous)
| Max data rate | Up to 300 Mbps (2.4 GHz) + 1300 Mbps (5 GHz)
| Wi-Fi class | AC1600
| Antennas | Integrated omni-directional
| Antenna gain | ~2 dBi
| MIMO | 2×2 (2.4 GHz), 3×3 (5 GHz)
| Ethernet ports | 1 × 10/100/1000 Mbps (Gigabit)
| CPU | QCA9556, 720 MHz
| CPU cores | 1
| RAM | 64 MB
| Storage | 16 MB Flash
| Operating system | RouterOS (Level 4 license)
| Power supply | PoE-in (802.3af/at), 11–57 V
| Max power consumption | ~12 W
| Protection rating | IP54 (weatherproof)
| Operating temperature | -40°C to +70°C
| Mounting | Wall, ceiling, or pole mounting
| Cooling | Passive
| Dimensions | 185 × 85 × 30 mm
| MTBF | ~100,000 hours
| Certifications | CE, FCC, EAC, RoHS
10 | Previdia UltraVox 2/16 CAN, TCP/IP
| Product | Modular fire alarm and voice evacuation panel Previdia UltraVox 2/16 CAN TCP/IP
| Type | Addressable fire detection + EVAC (voice alarm) control panel
| Configuration | 2 loops standard, expandable up to 16 loops
| System architecture | Modular (IFM / IFAM modules on CAN BUS)
| Communication bus | CAN BUS (internal modules)
| Network connectivity | TCP/IP Ethernet + RS485 (Hornet+) + IDANet
| BMS integration | Modbus TCP/IP, BACnet support
| Networking capacity | Up to 48 panels in one system
| Power supply | 90–264 VAC, 50/60 Hz
| Output voltage | ~26–27.6 V DC
| Power capacity | 1000 W per PSU (expandable up to 4000 W)
| Battery backup | 2 × 12 V (17–38 Ah typical)
| Loop type | Addressable loops (detectors, modules)
| Max modules | Up to 32 internal modules per system
| Voice evacuation | Integrated EVAC system (EN54-16 compliant)
| Audio system | 100 V speaker lines with supervision
| Amplifiers | 250 W modular amplifiers
| Control interface | Touch display (front panel)
| Protocols | TCP/IP, Modbus, proprietary INIM
| Cloud connectivity | INIM Cloud (remote monitoring)
| Protection rating | IP30
| Operating temperature | -5°C to +40°C
| Installation | Wall-mounted cabinet (expandable multi-cabinet system)
| Functions | Fire detection, alarm, evacuation, PA, system monitoring
11 | FPMCPU front CPU module (or equivalent)
| Product | FPMCPU front CPU module (or equivalent)
| Type | Main control unit (front panel CPU module)
| Application | Previdia Ultra / UltraVox / Previdia Max fire alarm systems
| Function | Central control and coordination of all system modules
| Installation | Mounted on front panel of control cabinet
| System connection | CAN drive bus (internal communication)
| Display | Graphic color touchscreen (~7”)
| Control interface | Touch + buttons + LED indicators
| CPU architecture | Dual CPU (main + backup)
| Redundancy | Built-in backup CPU ensures basic operation in case of failure
| Role modes | Main unit / backup unit / remote repeater
| Ethernet | Yes (TCP/IP for networking & remote control)
| RS485 interfaces | 2 channels: repeater + BMS (Modbus RTU)
| USB port | Mini-USB for configuration
| Serial port | RS232 for programming
| microSD slot | Yes (data storage / configuration)
| Power supply | ~27.6 V DC (from PSU module)
| Power consumption | ~130–140 mA typical
| Operating temperature | -5°C to +40°C
| Number per panel | Up to 2 (main + backup)
| Repeater capacity | Up to 14 units as remote keyboards
| Housing | Plastic front module (light or dark grey)
| Series | FPM (Front Panel Modules)
12 | Ceiling loudspeaker SPI-C66100 (or equivalent)
| Product | Ceiling loudspeaker SPI-C66100 (or equivalent)
| Type | Ceiling-mounted loudspeaker for voice evacuation (EVAC)
| Application | Fire alarm / voice evacuation / PA systems
| Certification | EN54-24 compliant (fire safety standard)
| Speaker size | 6.5”
| Rated power | 6 W
| Power settings | 1.5 / 3 / 6 W (selectable)
| Operating voltage | 70 V / 100 V line
| Sound pressure level (SPL) | ~95 dB (1W @ 1 m)
| Frequency response | 130 Hz – 15 kHz
| Transformer | Built-in line transformer
| Mounting type | Flush ceiling mounting
| Fixing method | Spring clips (quick installation)
| Housing | Metal корпус with rear protection dome
| Front grille | Metal
| Terminals | Ceramic terminal block
| Protection | Thermal fuse (overload protection)
| IP rating | IP21
| Dimensions | ~200 × 100 mm
| Cut-out diameter | ~175 mm
| Weight | ~0.9 kg
| Color | White
| Installation environment | Indoor (Type A)
13 | Addressable optical smoke detector ES0020RE (or equivalent)
| Product | Addressable optical smoke detector ES0020RE (or equivalent)
| Type | Addressable photoelectric (optical) smoke detector
| Application | Fire detection in buildings (offices, public, residential)
| Detection principle | Optical (light scattering)
| System compatibility | INIM addressable fire alarm systems (Previdia / SmartLoop)
| Communication | Addressable loop communication
| Operating voltage | From loop (approx. 15–30 V DC)
| Current consumption | Low (typical for addressable detectors)
| LED indication | 360° dual LED (alarm indication)
| Remote indicator | Supported (remote LED output)
| Sensitivity | EN54 compliant, adaptive compensation for dust
| Isolation | Built-in short-circuit isolator
| Addressing | Automatic / software addressing
| Base compatibility | Compatible with standard INIM detector bases
| Operating temperature | -5°C to +40°C
| Humidity | Up to 95% RH (non-condensing)
| Protection rating | IP40 (with base)
| Material | Flame-retardant plastic
| Color | White
| Diameter | ~100 mm
| Height | ~50 mm (with base)
| Weight | ~100 g
| Certification | EN54-7 compliant (smoke detector standard)