## Arhitectural solutions
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Suspended ceilings made of prefabricated panels including grid system with physical and visual characteristics type Rockfon Artic E24 with partially visible structure and dimensions 600 x 600 x 15mm, class 1/C/0N according to EN 13964
2 | Plastic floors mounted on the existing substrate, cleaned, including PVC sills, in rooms with areas greater than 16 sqm, with PVC carpet glued with pre-bonded / Omogenius PVC carpet, thickness = 2-2,3 mm; change:PVC profile, PVC sill in PVC PVC connection profile R=30 mm - 0,6 m/m2. Color according to the design.
3 | Interior partitions made of aluminum profiles with mat sandwich filling composed of PU boards and 1 mm sheet metal on both sides. The windows will be made of 4+4 mm transparent triplex glass. Doors will be equipped with stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); C-3 7500x2150(h)
4 | Interior wooden doors in a can, with 2 mm metal frame, color RAL 7014 and 44 mm plywood laminated wood plywood canvas, color RAL 1014 with mat varnish. With 1 mm stainless steel protection plate at the bottom and 4+4 mm transparent triplex glass 4+4 mm and stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); UI-1 1150x2020(h)

## Elevator
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Elevator NIKAN 5000 MRL
| Model | 5000 MRL (Machine Room-Less)
| Type | Electric traction elevator
| Rated load | 630 kg
| Passenger capacity | 2 persons
| Number of stops | 3
| Rated speed | 1.0 m/s
| Drive system | Gearless traction machine
| Machine room | Without (MRL configuration)
| Control system | Microprocessor-based collective control
| Power supply | 380–400V, 3-phase, 50 Hz
| Door type | Automatic sliding doors (center opening)
| Door opening width | Minim 900 mm (standard for 630 kg) with access for persons with disabilities
| Cabin internal dimensions | Minim 1100 × 1400 mm (W × D)
| Shaft dimensions (min.) | Approx. 1600 × 1600 mm (acording drawings)
| Pit depth | Approx. 1200 mm (typical)
| Overhead height | Approx. 3600 mm (typical)
| Safety system | Overspeed governor, safety gear, door interlocks
| Drive control | VVVF (Variable Voltage Variable Frequency)
| Noise level | Low-noise operation
| Compliance | EN 81-20 / EN 81-50 (or local equivalent)
| Interior finish | Stainless steel (as per design)
| Lighting | LED ceiling lighting
| Emergency system | Emergency lighting & alarm
| Optional features | ARD (Automatic Rescue Device), GSM module, access control

## Water
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Public WC Pan (Side Outlet, Floor-Mounted)
| Product type | Floor-mounted WC pan for public/sanitary facilities
| Outlet type | Horizontal (side/back outlet)
| Installation type | Floor-standing
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, antibacterial glaze, easy to clean
| Flushing system | Washdown or rimless flushing system
| Flush volume | 6/3 L dual flush (or 6 L single flush)
| Cistern type | Close-coupled cistern mounted directly on the bowl
| Cistern material | Ceramic (matching bowl)
| Water inlet | Bottom or side inlet (½")
| Flush mechanism | Mechanical push-button (dual flush recommended)
| Seat and cover | Heavy-duty thermoplastic or duroplast, slow-close (optional)
| Fixing system | Floor fixing bolts with protective caps
| Trap type | P-trap (horizontal outlet)
| Outlet diameter | Ø100 mm
| Dimensions (approx.) | 650–700 mm (L) × 350–380 mm (W) × 750–800 mm (H)
| Water pressure range | 0.5 – 10 bar
| Color | White (standard)
| Compliance | EN 997 / EN 33 (European standards)
| Application | Public buildings, schools, offices, commercial spaces
2 | Public washbasin (lavatory) made of semi-porcelain / sanitary porcelain, mounted on pedestal, with PP siphon
| Product type | Washbasin for public sanitary facilities
| Installation type | Wall-mounted basin with full pedestal
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, hygienic, stain-resistant glaze
| Mounting method | Wall-fixed with anchor bolts; pedestal for aesthetic and pipe concealment
| Pedestal type | Full pedestal (ceramic), matching basin
| Basin dimensions (approx.) | 550–600 mm (W) × 450–500 mm (D)
| Height (installed) | Approx. 800–850 mm from finished floor level
| Tap hole | Single hole Ø35 mm (standard)
| Overflow | Integrated overflow system
| Waste outlet diameter | Ø45 mm
| Siphon | Bottle trap, polypropylene (PP), Ø32 mm
| Water supply connection | ½" flexible connectors
| Fixing kit | Included (bolts, plugs, caps)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 14688 (washbasins)
| Application | Public buildings, offices, schools, commercial premises
3 | Wall-Mounted Urinal (Sanitary Porcelain)
| Product type | Urinal for public sanitary facilities
| Installation type | Wall-mounted
| Mounting surface | Reinforced concrete wall
| Material | Sanitary porcelain, fully glazed
| Surface treatment | Smooth, hygienic, stain- and chemical-resistant glaze
| Flushing system | Top or rear inlet (exposed or concealed flush valve)
| Flush control | Manual push valve or automatic sensor (optional)
| Water consumption | 0.5 – 3.0 L per flush (depending on flush valve)
| Water inlet connection | ½"
| Outlet type | Horizontal or vertical outlet
| Waste outlet diameter | Ø50 mm
| Trap type | Integrated trap or external siphon
| Fixing system | Wall anchor bolts with concealed fixings
| Installation height | Rim approx. 600–650 mm above finished floor level
| Dimensions (approx.) | 300–360 mm (W) × 300–350 mm (D) × 500–600 mm (H)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 13407 (urinals)
| Application | Public buildings, schools, offices, commercial facilities
4 | Chrome-Plated Mixer Tap with Swivel Spout (Public Toilets)
| Product type | Basin mixer tap for public sanitary facilities
| Installation type | Deck-mounted (single-hole installation)
| Body material | Brass (CuZn), chrome-plated finish
| Surface finish | Polished chrome, corrosion-resistant
| Spout type | Swivel (pivoting) spout
| Spout reach | Approx. 150–200 mm
| Cartridge type | Ceramic cartridge, 35–40 mm
| Control type | Single-lever mixer
| Water supply connection | Flexible hoses ½"
| Aerator | Anti-limescale aerator, M24/M22
| Flow rate | 5–9 L/min (depending on pressure)
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Water temperature range | 5°C – 90°C
| Fixing system | Mounting kit included (gasket, fixing nut, bolts)
| Application | Public toilets, schools, offices, commercial buildings
| Compliance | EN 817 (mechanical mixer taps)
5 | Accessible Wall-Mounted Bath Mixer with Hand Shower
| Product type | Bath mixer tap with hand shower for accessible sanitary rooms
| Installation type | Wall-mounted
| Mounting surface | Brick masonry wall (with concealed pipe connections)
| Body material | Brass (CuZn), chrome-plated
| Surface finish | Polished chrome, corrosion-resistant
| Control type | Single-lever mixer with extended ergonomic handle (accessible use)
| Cartridge type | Ceramic cartridge, 35–40 mm
| Temperature limiter | Adjustable safety stop (anti-scald protection)
| Diverter | Integrated automatic diverter (bath/shower)
| Shower hose | Flexible stainless steel or reinforced PVC, length 1500–2000 mm
| Hand shower | Ergonomic hand shower, anti-limescale nozzles
| Water inlet connection | ½" standard eccentric connections
| Flow rate | 8–12 L/min
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Temperature range | 5°C – 90°C
| Installation height | According to accessibility standards (approx. 900–1100 mm from finished floor)
| Accessibility compliance | EN 12182 / EN 1111 (if thermostatic version)
| Safety features | Anti-scald device, smooth edges, easy-grip lever
| Application | Public buildings, accessible sanitary units, healthcare facilities
| Color | Chrome (standard)
6 | Motorized Valve HL710.2 EPC
| Product name | HL710.2 EPC motorized valve
| Type | Electrically operated backwater / drain shut-off valve
| Nominal diameter | DN110 (Ø110 mm)
| Installation | Horizontal installation in drainage pipeline
| Housing material | High-strength polymer (PP/ABS), corrosion-resistant
| Valve flap material | Stainless steel / reinforced composite
| Drive type | Electric motor actuator
| Rated power (P) | 0.1 kW
| Supply voltage (U) | 220 V AC, 50 Hz
| Control system | Electronic control unit (EPC)
| Operating mode | Automatic closing in case of backflow; manual emergency operation
| Protection class | IP54 (or equivalent)
| Temperature range | 0°C to +60°C (wastewater applications)
| Application | Protection against sewer backflow in buildings
| Maintenance access | Removable cover for inspection and cleaning
| Compliance | EN 13564 (anti-flooding devices for buildings)
7 | Drainage pump Wilo-Drain TS/TSW 32,
| Product name | Wilo-Drain TS/TSW 32
| Type | Submersible drainage pump for wastewater (with fecal matter)
| Rated power (P) | 0.3 kW
| Supply voltage (U) | 230 V, 1~ (single-phase), 50 Hz
| Rated head (Hₚomp.) | 8 m
| Maximum flow rate | Up to approx. 10 m³/h (depending on model variant)
| Discharge connection | DN32 (Ø32 mm)
| Maximum submersion depth | Approx. 7 m
| Max. fluid temperature | Up to +35°C (short-term up to +60°C)
| Impeller type | Vortex or multichannel impeller (depending on TS / TSW version)
| Housing material | Stainless steel
| Motor protection | Integrated thermal motor protection
| Protection class | IP68
| Insulation class | F
| Cable length | Approx. 10 m (with plug)
| Operation mode | Automatic operation via float switch

## HAVC
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Steel Panel Radiator Type “KORADO 22K 500×1000
| Product type | Steel panel radiator
| Model | Type 22K (two panels + two convectors)
| Dimensions (H × L) | 500 × 1000 mm
| Depth | Approx. 100 mm
| Material | Cold-rolled steel panels
| Surface finish | Powder-coated, white (RAL 9016 standard)
| Heat output (90/70/20°C) | Approx. 1850 W
| Heat output (75/65/20°C) | Approx. 1450 W
| Maximum operating temperature | 110°C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Water content | Approx. 5–6 liters
| Weight | Approx. 25–26 kg
| Connections | 4 × G 1/2" female threaded (side connections)
| Installation type | Wall-mounted (brackets included)
| Air vent & plug | Included
| Standard compliance | EN 442
2 | steel panel radiator “KORADO Type 33K 500×1100
| Product type | Steel panel radiator
| Model | Type 33K (three panels + three convectors)
| Dimensions (H × L × D) | 500 × 1100 × ~155 mm
| Material | Cold-rolled steel panel construction
| Surface finish | Powder-coated white (standard RAL, corrosion-protected)
| Heat output (90/70/20 °C) | ~2914 W
| Heat output (75/65/20 °C) | ~2287 W
| Water content | ~8.36 L
| Weight | ~50.5 kg
| Maximum operating temperature | 110 °C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Connections | 4 × G 1/2″ internal threads
| Connecting pitch | H – 54 mm
| Installation type | Wall-mounted radiator
| Compliance | EN 442 (European radiator standard)
3 | Danfoss Thermostatic Radiator Valve with Pre-Setting RTR-N, DN 15
| Product type | Thermostatic radiator valve with pre-setting
| Model | RTR-N
| Nominal diameter | DN 15 (≈ 1/2″)
| Connection type | Rp 1/2″ internal thread
| Valve configuration | Normal flow type (presetting on the radiator inlet)
| Body material | Brass with corrosion-resistant surface finish
| Presetting | Integrated presetting ring with adjustable Kv steps
| Kv range | Approx. 0.04 – 0.7 m³/h (depending on presetting position)
| Kv at presetting “N” | Approx. 0.73 m³/h
| Max. operating temperature | Up to 120 °C
| Max. working pressure | 10 bar
| Test pressure | 16 bar
| Seal material | EPDM or equivalent elastomer
| Differential pressure tolerance | Up to ~0.6 bar for stable control
| Surface finish | Nickel-plated or chrome plated (depending on manufacturer)
| Standards compliance | EN 215 (Thermostatic radiator valves)
| Accessories | Compatible with thermostatic heads (RA, RAS series or equivalent)
| Country of manufacture | Denmark (Danfoss)
4 | Danfoss Radiator Shut-off Valve (RLV), DN 15
| Product type | Radiator shut-off / lockshield valve
| Model | RLV, DN 15
| Connection size | R 1/2″ (internal thread) – radiator and system connections
| Design | Straight lockshield valve
| Body material | Brass with nickel-plated finish (corrosion-resistant)
| Maximum operating temperature | 120 °C
| Maximum working pressure | 10 bar
| Test pressure | 16 bar
| Kv (flow coefficient) | Approx. 2.20–2.50 m³/h
| Seal material | EPDM or equivalent
| Surface finish | Nickel plated
| Thread standard | ISO 7/1 (R 1/2″)
| Type variants | Straight or angled, standard or self-sealing tailpiece
| Country of manufacture | Denmark (Danfoss)
5 | Thermostatic Element Danfoss RTR 7090
| Model / Part No. | RTR 7090 / 013G7090
| Type | Thermostatic radiator thermostat element
| Application | For automatic temperature control of radiator valves
| Compatibility | Designed for RTR series radiator valves (e.g., RTR-N, RTR-G), can be combined with appropriate radiator valve bodies
| Sensing element | Gas-filled bulb sensor
| Mounting / Connection | Clip-on type (quick clip fitting to valve)
| Adjustment range (room air temperature) | 5 °C to 26 °C
| Temperature range, operational | Min. 5 °C – Max. 26 °C setpoint range
| Colour | White
| Max. permitted system temperature | Approx. 120 °C (typical TRV rating for paired valves)
| Max. working pressure | Approx. 10 bar (based on typical radiator thermostatic valve ratings)
| Ratio / Sensitivity | Proportional direct-acting thermostat with small proportional band
| Housing material | Plastic body with internal sensing element
| Warranty | Approx. 1 year
| Country of manufacture | Denmark (Danfoss)
| Standards compliance | EN 215 (when combined with compliant radiator valve)
6 | Gaicomini R551 Brass Distribution Manifold (DN 50 × 6)
| Product type | Distribution manifold / collector
| Model | R551 – Brass distribution manifold
| Nominal size | DN 50 (2 ″) main inlet/outlet connections
| Number of outlets | 6 circuits (6 derivations)
| Outlet connection size | Typically 1 ″ female threaded outlets (applicable to DN 50 variant)
| Material | Brass (CW605N)
| Outlet spacing | 100 mm center-to-center between outlets
| Temperature range | 5 °C – 110 °C
| Maximum working pressure | 16 bar
| Test pressure | Typically above working pressure (manufacturer standard)
| Connection thread type | Female threaded (G)
| Material grade | CW605N brass (corrosion-resistant)
| Mounting | Wall mounting with appropriate brackets ( R588P)
| Suitable fluid | Hot and chilled water (heating/cooling systems)
7 | Caleffi Ball Valve, PN 16, DN 25
| Product type | Ball shut-off valve (stop valve)
| Model / Series | Caleffi ball valve, PN 16, DN 25
| Nominal size | DN 25 (1″)
| Pressure rating | PN 16 (maximum working pressure 16 bar)
| Connection type | Threaded / flanged (depending on version)
| Body material | Brass (corrosion-resistant)
| Ball material | Brass, chrome-plated
| Seat / seals | PTFE (Teflon) seats
| Stem material | Stainless steel or brass
| Handle | Lever handle for manual operation
| Bore type | Full bore (unrestricted flow)
| Medium temperature range | Approx. –10 °C to +100 °C (typical for PN 16 valves)
| Suitable medium | Hot and cold water, glycol solutions, non-aggressive fluids
| Standards / Compliance | EN 12266 (valve testing), DIN/ISO standards for threaded/flanged connections
| Installation | Inline with pipework, vertical or horizontal
| Application | Heating systems, plumbing, hydronic circuits
8 | VENTS KR 125 Airflow Damper
| Product type | Round duct airflow damper / manual shutter
| Series | KR (round)
| Compatible duct diameter | 125 mm
| Body material | Galvanized steel
| Overall dimensions (approx.) | D: ~124 mm, B: ~195 mm, L: ~200 mm
| Weight | Approx. 0.82 kg
| Operation | Manual adjustment to regulate airflow
| Connection type | Fits circular duct Ø125 mm
| Application | Airflow regulation in ventilation ducts
| Finish | Galvanized / corrosion-protected
9 | Brofer PDZ-2 AQN 225×225
| Product type | Ceiling 4-way air diffuser – AQN series
| Dimensions | 225 × 225 mm panel size
| Material | Aluminium, powder-coated white (RAL 9010 / RAL 9016)
| Installation | Ceiling supply or return air diffuser
| Recommended ceiling height | 2.5 – 3.1 m
| Fixing | Screws on diffuser neck (concealed)
| Central core | Removable
| Accessories | Galvanized steel plenums, calibration dampers
10 | Water-to-Air Convector with EC Fan (Volcana VR Mini EC)
| Duct type | Water-to-air convector (fan coil / hydronic convector)
| Model / Series | Volcana VR Mini EC (with EC controller)
| Heating capacity | 3 – 20 kW (depending on heat exchanger size, water inlet/outlet temps & air flow)
| Airflow range | Up to 2100 m³/h
| Fan motor power | 0.095 kW
| Fan rotation speed | 1450 rpm
| Fan type | EC (Electronically Commutated) motor with high efficiency and variable speed control
| Supply voltage | 230 V AC, 50 Hz
| Control | Integrated EC controller with variable speed / airflow adjustment
| Heat exchanger | Copper tubes with aluminium fins
| Connection type | Hydronic water connections (in/out)
| Water side working pressure | Typically up to 10 bar (project dependent)
| Water temperature range | 40 – 90 °C (typical for convectors; actual range per manufacturer)
| Filter | Washable air filter (removable)
| Housing material | Steel / aluminium with corrosion-resistant finish
| Mounting | Floor standing or recessed (depending on unit type)
| Terminals / Controls | EC controller with speed / airflow setting; optional room thermostat
| Noise level | Dependent on airflow / fan speed (EC motors - low-noise)
| Insulation | Thermal / condensate insulation on water coil housing
| Standards / Compliance | CE certification; electrical safety (EN)
11 | Atrea Heat Recovery Ventilation System (Supply & Extract) Duplex 5000 Multi-V
| Product type | Mechanical ventilation unit with heat recovery (HRV/ERV)
| Model / Series | Duplex 5000 Multi-V
Supply (Refulare)
| Airflow (L) | 3,670 m³/h
| Static pressure | 450 Pa
| Fan power | 3.30 kW
| Fan speed | 2,700 rpm
| Current draw (I) | 5.4 A
| Supply voltage (U) | 400 V, 3-phase
Extract (Aspiratie)
| Airflow (L) | 3,195 m³/h
| Static pressure | 450 Pa
| Fan power | 3.30 kW
| Fan speed | 2,700 rpm
| Current draw (I) | 5.4 A
| Supply voltage (U) | 400 V, 3-phase
| Heat recovery type | Counterflow / plate heat exchanger (high efficiency)
| Heat recovery efficiency | Typically 60–85 % (depending on model)
| Control | Integrated control panel with variable fan speeds
| Bypass | Summer bypass (optional)
| Filters | Supply & extract filters (G4 / F7 class or equivalent)
| Housing material | Galvanized steel with thermal/acoustic insulation
| Insulation | Internal panels with anti-condensation insulation
| Duct connections | Circular or rectangular spigots as per design
| Noise level | Depends on duct design & fan speed
| Protection class | IP rating (commonly IP34 or higher)
| Application | Ventilation with heat recovery for commercial / public buildings
| Standards / Compliance | CE compliant, EN standards for ventilation & energy recovery
12 | Atrea Heat Recovery Ventilation System (Supply & Extract) Duplex 3500 Multi-V
| System type | Mechanical ventilation unit with heat recovery (HRV)
| Model / Series | Duplex 3500 Multi-V
Supply (Refulare)
| Airflow | 2,195 m³/h
| Static pressure | 450 Pa
| Fan power | 2.50 kW
| Fan speed | 2,970 rpm
| Current draw | 3.8 A
| Supply voltage | 400 V, 3-phase
Extract (Aspiratie)
| Airflow | 2,195 m³/h
| Static pressure | 450 Pa
| Fan power | 2.50 kW
| Fan speed | 2,970 rpm
| Current draw | 3.8 A
| Supply voltage | 400 V, 3-phase
| Heat recovery core | Counterflow / plate or rotary wheel (high efficiency)
| Heat recovery efficiency | Typically 60–85 % (application-dependent)
| Control system | Integrated control panel with speed stages
| Filters | Supply and extract filters (e.g., G4/F7 or equivalent)
| Housing | Galvanized steel with internal thermal/acoustic insulation
| Duct connection | Circular/rectangular spigots to match duct system
| Bypass | Optional automatic summer bypass
| Noise level | Dependent on airflow and installation design
| Protection class | Usually IP rating suitable for mechanical rooms
| Application | Ventilation with energy recovery in commercial/public spaces
| Standards / Compliance | CE marked; compliant with EN ventilation standards
13 | Systemair HELMER-60-NO-140-K-MB24-0 Fire/Smoke Damper
| Product type | Fire and smoke damper – normally open (NO)
| Series | HELMER-60-NO-K
| Model example | HELMER-60-NO-140-K-MB24-0
| Manufacturer | Systemair (or equivalent)
| Application | Fire and smoke protection in ventilation ducts
| Configuration | Channel/round duct installation
| Diameter | Ø 140 mm (nominal) for circular ducts
| Operation mode | Normally open – closes on fire signal
| Actuator type | Electromechanical actuator (Belimo MB24 V DC)
| Supply voltage | 24 V DC (MB24)
| Fire resistance rating | EI 60 (60 min fire resistance typical)
| Material | Galvanized steel housing
| Section shape | Round duct connection
| Ambient temperature range | Typically –30 °C to +40 °C during normal operation
| Medium airflow | Designed for air handling in ventilation systems
| Drive mechanism | Electromechanical with return spring
| Manual release/testing | Manual release handle/pin for testing
| Safety function | Closes on signal from fire alarm system
| Mounting | Installed directly in circular ventilation ducts
| Standards & compliance | Fire damper standards for HVAC systems
14 | Manual Flow Regulator for Hydronic Balancing (REG-L)
| Product type | Manual flow regulator / hydraulic balancing valve
| Model / Series | REG-L (VEZA or equivalent)
| Application | Balancing and regulation of water flow in hydraulic circuits (heating, cooling, radiant systems)
| Design | Inline manual valve with calibrated scale for flow setting
| Connection sizes | Typically available in DN15 – DN50 (project-specific size)
| Connection type | Threaded (Rp / G), compression, or flanged (depending on variant)
| Flow range | Adjustable range depending on size (e.g., 0.1–5.0 m³/h for DN15/DN20; higher for larger sizes)
| Body material | Brass / bronze (CW617N / CW602N)
| Operating temperature | –10 °C to +120 °C (typical HVAC hydronic range)
| Maximum working pressure | 10–16 bar (project dependent)
| Presetting scale | Graduated scale for manual balancing (flow or Kv setting)
| Actuator type | Manual handwheel / built-in adjustment screw
| Seals | EPDM (standard), high-temperature options available
| Flow characteristic | Linear or equal percentage (depending on model)
| Standards / Compliance | Complies with EN valve standards for hydronic systems
| Serviceability | Easy access for balancing and readjustment without system shutdown
15 | Hot Air Heating Coil T3500 3R / Type 2
| Product type | Forced-air heating coil (hot air battery)
| Model / Series | T3500 3R / Type 2
| Application | Pre-heating or reheating in ventilation / air handling systems
| Heat transfer medium | Hot water (hydronic heating system)
| Design water temperature (max) | Typically 90–105 °C (project-dependent)
| Design water pressure (max) | Up to 10–16 bar (standard hydronic rating)
| Coil circuit type | 3-row (3R) finned heat exchanger
| Rows / Circuit | 3 rows of tubes for higher heat transfer
| Tube material | Copper tubes (standard HVAC grade)
| Fin material | Aluminium fins (corrugated / bonded)
| Connection type | Threaded / flanged water inlet & outlet
| Connections size | Project-specific (e.g., DN25 / 1″, larger as required)
| Airflow range | Dependent on fan / system design
| Heat output range | Project-dependent (based on water ΔT and airflow)
| Housing / casing | Galvanized steel or painted steel for mechanical strength
| Drain pan | Optional condensate drip tray (if cooling duty included)
| Fin spacing | Standard (≈ 2–3 mm), other spacings on request
| Pressure drop (water side) | Depends on circuit velocity and coil size
| External static pressure capability | Designed for integration with ducted fans
| Mounting | Between duct sections or in AHU heater section
| Standards / Compliance | EN 13053 (AHU coils), ASHRAE guidelines for coil design
| Insulation | Optional thermal/acoustic insulation on casing
16 | Noise Attenuator (Duct Silencer) LDR-900-250-950
| Product type | Ventilation noise attenuator / duct silencer
| Model (example) | LDR-900-250-950 (or equivalent round silencer)
| Duct connection diameter | 250 mm (nominal)
| Overall length | ~900 – 950 mm
| Casing material | Galvanized steel (durable, corrosion-resistant)
| Internal absorption | Non-flammable sound-absorbing material (e.g., mineral wool)
| Inner core | Perforated inner tube to support acoustic lining
| Connection type | Flanged or spigot collar with rubber seal for airtight duct connection
| Installation position | Installed inline in round air ducts; can be oriented in any position
| Application | Reduces noise produced by ventilation equipment (fans, AHUs) transmitted through ducts
| Use in system | Supply and extract ventilation ducts in HVAC installations
| Noise reduction | Typical attenuation increases with frequency (depends on exact design and length) — e.g., ~15–30 dB at mid-frequencies (500–1000 Hz) in similar silencers
| Pressure drop | Low pressure drop typical for straight silencer at designed airflow (specific data per manufacturer)
| Temperature range | Suitable for normal HVAC air temperatures (typically up to ~80–100 °C, depending on insulation type)
| Fire / Safety | Sound-absorbing lining typically non-combustible (mineral wool)
| Mounting hardware | Clamps / flanges for connection to round ductwork included or specified
17 | Vents Exhaust Ventilation System (Rectangular) with Fan
| System type | Exhaust ventilation system
| Airflow (L) | 1,425 m³/h
| Static pressure (P) | 300 Pa
| Fan type | Rectangular ventilation fan (inline or plenum mounted)
| Fan model | Vents VKPF 4D 500×300 series
| Fan power (N) | 0.855 kW
| Fan speed (n) | 1,300 rpm
| Current (I) | 1.70 A
| Supply voltage (U) | 400 V, 3-phase
| Fan housing | Rectangular steel casing with flange connections
| Impeller type | Backward-curved centrifugal wheel (high efficiency)
| Motor type | IE2 / IE3 induction motor (air handling duty)
| Mounting | Elastic anti-vibration mounts (included)
| Elastic support type | Elastic anti-vibration supports (VKPF 4D 500×300 or equivalent)
| Installation position | Inline in rectangular duct (horizontal/vertical as specified)
| Control / Speed | Suitable for external VFD control (optional)
| Noise level | Not higher than 40 db
| Protection class | Typically IP44 or higher (project dependent)
| Operating temperature | Ambient to +40 °C (standard ventilation use)
| Finish | Galvanized or painted steel
| Application | Exhaust / extract air ventilation in commercial/public buildings
| Standards / Compliance | CE marked; complies with relevant EN & IEC standards for fans
18 | Soler & Palau SILENT-100 Bathroom Extract Fan
| roduct type | Bathroom axial extractor fan (quiet operation)
| Model / Series | SILENT-100 (e.g., Soler & Palau SILENT‑100 CZ)
| Airflow | Approx. 55–95 m³/h (typical units in the SILENT-100 family deliver up to ~95 m³/h free airflow)
| Static pressure | Approx. 20 Pa at lower airflow conditions (typical axial bathroom fan characteristics)
| Motor power | 0.008 kW (8 W)
| Motor speed | ≈2400 rpm
| Supply voltage | 230 V AC, 50 Hz
| Operating current | ~0.07–0.08 A
| Noise level | Approx. 26.5 dB(A) @ free air
| Connection Ø | 100 mm duct (compatible with ~99–100 mm round ducts)
| Protection class | IP45 (splash-water resistant)
| Insulation class | Class II (double-insulated)
| Motor bearing | Ball bearings – long life and quiet operation
| Backdraft shutter | Integrated non-return/backdraft shutter included
| Mounting | Wall or ceiling installation
| Operating temperature | Up to ~+40 °C
| Housing material | Durable plastic with silent-block motor mounts
| Dimensions (approx.) | ~158 × 158 × 109 mm
| Weight | ~0.57 kg
| Application | Small bathroom / WC / wet room ventilation
| Optional features | Timer, humidistat, presence sensor (on specific variants)
19 | Overpressure ventilation system with a rectangular fan Vents VKPF 4D 500×250
| System type | Overpressure ventilation (supply/pressurization fan)
| Airflow (L) | 1,500 m³/h
| Static pressure (P) | 250 Pa
| Fan type | Rectangular centrifugal / plenum fan
| Fan motor power (N) | 0.57 kW
| Fan speed (n) | 1,270 rpm
| Current (I) | 0.94 A
| Supply voltage (U) | 380–400 V, 3-phase
| Fan housing | Rectangular steel casing with flanged connections
| Impeller | Backward-curved centrifugal wheel (for higher static pressure efficiency)
| Motor type | IE2 / IE3 three-phase induction motor for continuous duty
| Mounting | Elastic anti-vibration support VKPF 4D 500×250 (or equivalent) supplied
| Duct connection | Rectangular spigots (500×250 mm approximate interface)
| Control / Speed | Suitable for VFD / external speed control (optional)
| Noise level | Dependent on installation, fan speed, and duct design
| Protection class | Typically IP44 or higher (project dependent)
| Operating temperature | Up to ~+40 °C (standard HVAC duty)
| Finish | Galvanized or painted steel (corrosion resistant)
| Application | Supply / overpressure ventilation in buildings, stairwells, corridors, etc.
| Standards / Compliance | CE compliant; EN & IEC standards for fans and motors
20 | Outdoor Unit & System (PSA-RP71 KA / SUZ-M71VA)
| roduct type | Outdoor condensing unit for split air conditioner
| Model | SUZ-M71VA (paired with PSA-RP71 KA series)
| Cooling capacity | Approx. 7.1 kW (nominal)
| Heating capacity | Approx. 7.6–8.0 kW
| Refrigerant | R32
| SEER (Seasonal Cooling Efficiency) | ~6.2 – 6.5 (A++ class)
| SCOP (Seasonal Heating Efficiency) | ~4.0 (A+ class)
| Seasonal energy class | Cooling: A++ / Heating: A+
| Sound power level (outdoor) | ~66 dB(A)
| Operating range – cooling | –15 °C to +46 °C outdoor
| Operating range – heating | –10 °C to +24 °C outdoor
| Max. refrigerant piping length | 30 m
| Max. height difference (indoor–outdoor) | 30 m
| Refrigerant pipe sizes | Liquid: ~9.5 mm / Gas: ~15.9 mm
| Airflow (approx.) | ~50.1 m³/min (~3000 m³/h)
| Dimensions (W×D×H) | 840 × 330 × 880 mm
| Weight | ~53–55 kg
| Power supply | 230–400 V / 1~ / 50 Hz (project specific)
| Features | Inverter compressor, high efficiency, low noise

## Electrical
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Recessed LED Panel, 600×600 mm, 35 W, 4000 K
| Product type | Recessed LED ceiling luminaire (LED panel)
| Model / Format | 600 × 600 mm (suitable for 600×600 mm ceiling grid)
| Rated power | 35 W
| Light source | Integrated LED modules
| Color temperature | 4000 K (neutral white)
| Rated luminous flux | ≈ 3000–3500 lm (typical from a 35 W panel)
| Efficacy | ≈ 85–100 lm/W (dependent on manufacturer)
| CRI (Color Rendering Index) | ≥ 80 (≥ Ra80)
| Beam angle | ≈ 120° (wide uniform distribution)
| Driver type | External / integrated LED driver (electronic)
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut, manufacturer dependent)
| Housing material | Aluminium frame + steel back housing
| Diffuser / Optics | Opal / microprismatic diffuser for uniform glare-free light
| Mounting type | Recessed into suspended ceiling grid (T-bar)
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistance)
| Operating temperature | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80 B10)
| Certifications | CE
| Finish / Color | White frame (powder coated)
2 | Linear LED Light, 1200 mm, 45 W, 4000 K
| Product type | Linear LED luminaire
| Length | 1200 mm
| Rated power | 45 W
| Light source | Integrated LED
| Color temperature | 4000 K (neutral white)
| Luminous flux | ≈ 3900–4500 lm (typical from a 45 W LED)
| Efficacy | ≈ 85–100 lm/W (dependent on model)
| Color rendering (CRI) | ≥ 80 (≥ Ra80)
| Beam angle | 120° (wide light distribution)
| Driver type | Built-in / external electronic LED driver
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut – model dependent)
| Housing material | Aluminium body with steel end caps
| Diffuser | Opal or prismatic polycarbonate for uniform light
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistant)
| Operating ambient temp | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80)
| Finish / Color | White (standard)
| Certifications | CE, RoHS, EMC
| Application | Offices, corridors, retail, education, industrial interiors
3 | Illuminated Direction Indicator with Battery
| Product type | Illuminated directional indicator / emergency exit arrow sign
| Rated LED power | 3 W
| Light source | High-efficiency LEDs
| Illumination color | Green (standard for emergency direction signs)
| Symbol / Arrow type | Directional arrow or pictogram (configurable: left / right / up / down)
| Supply voltage | 220–240 V AC, 50 Hz (primary mains)
| Backup power | Rechargeable battery (internal)
| Battery type | Sealed lead-acid (SLA) or NiMH (model dependent)
| Battery autonomy | ≥ 3 hours (in emergency mode)
| Charge time | ≤ 24 hours to full charge
| LED lifetime | ≥ 50,000 h
| Viewing distance | ≥ 20–25 m (depending on size and installation)
| Ingress protection | IP20 (indoor), optional higher rating on request
| Mounting | Wall or ceiling (surface mounted)
| Housing material | ABS / polycarbonate flame-retardant enclosure
| Operating temperature | 0 °C to +40 °C (typical)
| Emergency testing | Built-in test button (optional)
| Standards / Compliance | Compliant with EN 50172 / EN 1838 (emergency lighting)
| Indicators | Charge / test LED indicators
| Finish / Color | White housing (standard)
4 | Distribution Board, 36 Modules (Flush-Mounted)
| Product type | Electrical distribution board (consumer unit)
| Model / Type | Flush-mounted distribution board, 36 modules (ЩРв-36 or equivalent)
| Installation type | Recessed / flush-mounted (in-wall installation)
| Number of modules | 36 DIN modules (3 rows × 12 modules typical)
| Rated voltage | 230/400 V AC, 50 Hz
| Rated current | Up to 63–100 A (depending on manufacturer)
| Protection class | IP30–IP40 (indoor use)
| Impact resistance | IK07 (typical)
| Material | Metal enclosure with powder coating or high-quality ABS (model dependent)
| Door type | Solid or transparent hinged door
| Mounting rail | Standard 35 mm DIN rail
| Neutral busbar (N) | Included
| Protective earth busbar (PE) | Included
| Terminal type | Screw terminals
| Cable entry | Top and bottom knockouts
| Operating temperature | –5 °C to +40 °C
| Color | White (RAL 9016 typical)
| Standards / Compliance | IEC 61439-1 / IEC 61439-3, CE
5 | Residual Current Circuit Breaker with Overcurrent Protection (RCBO), 2P, C16A, 10 mA, 6 kA
| Product type | RCBO (Residual Current Circuit Breaker with Overcurrent protection)
| Number of poles | 2P (Phase + Neutral)
| Rated current (In) | 16 A
| Tripping characteristic | Type C (magnetic curve C)
| Rated residual current (IΔn) | 10 mA
| Breaking capacity | 6 kA
| Rated voltage (Ue) | 230 V AC
| Frequency | 50/60 Hz
| Residual current type | Type AC or Type A (model dependent)
| Mounting | 35 mm DIN rail
| Protection degree | IP20 (installed in enclosure)
| Mechanical endurance | ≥ 10,000 operations
| Electrical endurance | ≥ 4,000 operations
| Terminal type | Screw clamp terminals
| Standards | IEC 61009-1
6 | Uninterruptible Power Supply (UPS), 4 kVA
| Product type | Uninterruptible Power Supply (UPS)
| Rated power capacity | 4 kVA
| Active power (typical) | 3.2–3.6 kW (depending on power factor 0.8–0.9)
| UPS topology | Online double-conversion / Line-interactive (model dependent)
| Input voltage | 220–240 V AC
| Input frequency | 50/60 Hz (auto sensing)
| Output voltage | 230 V AC ±1–2%
| Output frequency | 50/60 Hz ±0.1 Hz (online type)
| Waveform | Pure sine wave
| Transfer time | 0 ms (online) / 2–10 ms (line-interactive)
| Battery type | Sealed lead-acid (VRLA) or external battery pack
| Battery autonomy | 5–15 minutes at full load (extendable with external batteries)
| Recharge time | 4–8 hours to 90% capacity
| Bypass | Automatic and manual bypass (model dependent)
| Efficiency | ≥ 90% (online), ≥ 95% (eco mode)
| Protection features | Overload, short-circuit, battery deep discharge, overtemperature
| Communication ports | USB / RS-232 / SNMP (optional network card)
| Display | LCD display with load and battery status
| Cooling | Forced air cooling (internal fans)
| Installation type | Tower or Rack-mount (model dependent)
| Protection class | IP20 (indoor use)
| Operating temperature | 0 °C to +40 °C
| Standards / Compliance | IEC 62040-1, IEC 62040-2, CE

## Low voltage
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB 26 -03131 Capital repair and modernization of the “Mihai Eminescu” Theoretical Lyceum from Cimislia town.
1 | Videoregistrator 2U 4K NVR, 128-ch IP camera inputs, 2-ch@32 MP/2-ch@24 MP/4-ch@12 MP/8-ch@8 MP/16-ch@4 MP/32-ch@1080p, 2 HDMI, 2 VGA, 8K or dual 4K video outputs,
| Product type | Network Video Recorder (NVR)
| Form factor | 2U rack-mount
| IP camera inputs | 128 channels
| Max recording resolution | Up to 32 MP
| Decoding capability | 2-ch @ 32 MP / 2-ch @ 24 MP / 4-ch @ 12 MP / 8-ch @ 8 MP / 16-ch @ 4 MP / 32-ch @ 1080p
| Video outputs | 2 × HDMI, 2 × VGA
| Display resolution | Up to 8K (7680×4320) or dual 4K (3840×2160) output
| Video compression | H.265+ / H.265 / H.264+ / H.264
| Recording bandwidth (incoming) | Typically up to 400–512 Mbps (model dependent)
| Outgoing bandwidth | Up to 400 Mbps (model dependent)
| Audio support | 2-way audio (RCA), IP camera audio
| Hard drive bays | 8–16 SATA interfaces (model dependent)
| Max storage capacity | Up to 10–16 TB per HDD (model dependent)
| RAID support | RAID 0/1/5/6/10 (enterprise models)
| Network interface | 2 × RJ45 10/100/1000 Mbps (Gigabit)
| USB ports | USB 2.0 / USB 3.0
| Alarm inputs/outputs | Multiple alarm I/O (model dependent)
| Smart functions | Motion detection, intrusion detection, face recognition, smart analytics (AI models)
| Remote access | Web browser, CMS software, mobile app
| Power supply | 100–240 V AC, 50/60 Hz
| Power consumption | Approx. 30–60 W (without HDDs)
| Operating temperature | -10 °C to +55 °C
| Protection class | Indoor use
2 | Hikvision DS‑2CD1067G2‑LUF (a 6 MP outdoor/indoor fixed network camera with built-in mic and audio support
| Product type | Fixed network (IP) dome camera
| Image sensor | 1/2.7″ Progressive CMOS
| Resolution | 6 MP (3072 × 2048)
| Lens | Fixed 2.8 mm (wide) / optional 4 mm variants
| Field of View (approx.) | 102° (H) × 55° (V) × 124° (D)
| Min. Illumination | 0.01 lux @ (F1.2, AGC ON)
| Day/Night | IR cut filter with auto switch
| IR Range | Up to 10–15 m (model dependent)
| Video Compression | H.265 / H.264 / MJPEG
| Max. Frame Rate | 6 MP @ 20 fps
| Video Streaming | 3 concurrent streams
| WDR | Digital WDR (Wide Dynamic Range)
| BLC / HLC | Yes (Backlight / Highlight compensation)
| Noise Reduction | 3D Digital Noise Reduction (3D DNR)
| Audio | Built-in microphone
| Network | 1 × RJ45 10/100 Mbps
| PoE | 802.3af PoE (power over Ethernet)
| Storage | MicroSD/SDHC/SDXC card slot (up to 256 GB)
| Smart features | Motion detection, region of interest, privacy mask
| ONVIF | Profiles S/G compatible
| Power | PoE or 12 V DC
| Operating Temp. | –30 °C to +60 °C
| Ingress Protection | IP67 (dust & water resistant)
| IK Rating | IK10 (impact resistant)
| Housing material | Metal / plastic weatherproof casing
| Dimensions | Approx. Ø109 × 78 mm
| Weight | ~0.4 kg
3 | Hikvision DS-2CD1147G2H-LIU(F), a 4 MP network camera with built-in IR and advanced features
| Product type | Network (IP) turret camera
| Image sensor | 1/3″ Progressive Scan CMOS
| Effective pixels | 4 MP (2688 × 1520)
| Lens | 2.8 mm fixed lens (horizontal FOV ~102°)
| Maximum resolution | 2688 × 1520
| Min. illumination | 0.005 lux @ (F1.6, AGC ON)
| Day/Night | True D/N with mechanical IR cut filter
| IR illumination | Up to 30 m range (built-in IR LEDs)
| Video compression | H.265 / H.264 / MJPEG
| Max. frame rate | 4 MP @ 30 fps
| Video streams | 3 independent streams
| Wide Dynamic Range | Digital WDR (120 dB)
| Noise reduction | 3D DNR (Digital Noise Reduction)
| ROI / BLC / HLC | Yes (Region of Interest / Backlight / Highlight Comp)
| Audio | Built-in microphone
| Smart features | Motion detection, line crossing, intrusion detection (model dependent)
| Network | 1 × RJ45 10/100 Mbps
| Power | PoE (802.3af) or 12 V DC
| Power consumption | < 6 W typically
| On-board storage | MicroSD/SDHC/SDXC up to 256 GB
| Operating temp. | –30 °C to +60 °C
| Ingress protection | IP67 weatherproof
| Impact protection | IK10 vandal resistant
| Housing material | Metal base with plastic/metal dome
| Dimensions | Approx. Ø110 × 93 mm
| Weight | ~0.5 kg
4 | Hikvision DS‑3E1510P‑SI, an 8-port Gigabit PoE-capable network switch often used in IP camera systems
| Product type | Smart managed PoE network switch
| Brand / Model | Hikvision DS-3E1510P-SI
| Ports – Ethernet | 8 × Gigabit RJ45 PoE ports
| Ports – Uplink | 2 × Gigabit optical fiber (SFP) ports
| Switching capacity | 20 Gbps
| Packet forwarding rate | 14.88 Mpps
| MAC address table | 8 K entries
| Internal packet cache | 4.1 Mbits
| PoE standards | IEEE 802.3af / IEEE 802.3at
| PoE power per port | Up to 30 W per PoE port
| Total PoE budget | 110 W
| PoE power pins | End-span 1/2(+), 3/6(-)
| Long-range PoE | Ports 1–8 up to 300 m (extend mode)
| Surge protection | 6 kV on PoE ports
| Network functions | STP/RSTP, VLAN, SNMP, QoS, link aggregation
| PoE watchdog | Auto-detect & restart unresponsive cameras
| Operating temperature | 0 °C to 40 °C
| Storage temperature | –40 °C to 85 °C
| Operating humidity | 5 % to 95 % (no condensation)
| Power supply | 48 V DC, 2.5 A
| Max. power consumption | 120 W
| Idle power | ~7 W
| Dimensions (W×H×D) | 217.6 × 27.8 × 108.55 mm
| Weight | ~1.21 kg
| Installation | Desktop or wall mount
| Certifications | CE, FCC, UL, RoHS, WEEE, RCM
5 | Hikvision DS-3E1326P-EI/M
| Device Type | Smart Managed PoE Switch
| Ports (PoE) | 24 × 10/100 Mbps RJ45
| Uplink Ports | 1 × Gigabit RJ45 + 1 × Gigabit RJ45/SFP Combo
| PoE Standard | IEEE 802.3af / 802.3at
| Max PoE per Port | 30 W
| Total PoE Budget | 230 W
| Switching Capacity | 14.8 Gbps
| Packet Forwarding Rate | 11.01 Mpps
| MAC Address Table | 16K
| Packet Buffer | 4 Mbit
| VLAN Support | 802.1Q (up to 4094 VLANs)
| Link Aggregation | Static (1 group)
| Loop Prevention | STP / RSTP
| Long Range PoE Mode | Up to 300 m (with supported devices)
| PoE Watchdog | Yes (auto restart of unresponsive devices)
| Port Isolation | Yes
| Management | Web GUI, LLDP, Port Mirroring, Cable Diagnostics, Hik-Central / Hik-Partner Pro
| Surge Protection | 6 kV
| Power Supply | 100–240 VAC, 50/60 Hz
| Max Power Consumption | ~250 W
| Idle Consumption | ~20 W
| Operating Temperature | 0°C to +45°C
| Storage Temperature | −40°C to +85°C
| Humidity | 5–95% (non-condensing)
| Dimensions (W×H×D) | 440 × 44 × 220.8 mm
| Weight | ~2.13 kg
| Mounting | 19" Rack-mountable
6 | Hard Disk Drive (HDD) 8 TB SATA-III (3.5″ form-factor, internal storage)
| Capacity | 8 TB (≈ 8 000 GB)
| Interface | SATA-III (6 Gb/s)
| Form Factor | 3.5″
| Rotational Speed | 5400 rpm (desktop/consumer) / 7200 rpm (performance/enterprise)
| Cache (Buffer) | 128 MB – 256 MB
| Max Transfer Rate (SATA) | Up to 6.0 Gb/s
| Sustained Data Transfer | ~215 – 240 MB/s (model dependent)
| Mean Time Between Failures (MTBF) | ~1 M – 2.5 M hours (enterprise grade)
| Power Consumption (Typical) | ~5 – 9 W during read/write
| Idle Power | ~3 – 7 W
| Voltage | 5 V / 12 V (standard SATA power)
| Operating Temp. | ~0 °C – 60 °C
| Shock (Operating) | ~70 G
| Dimensions (W×D×H) | ~101.6 × 147 × 26.1 mm
| Weight | ~650 – 780 g
| Features | S.M.A.R.T., advanced power management, error recovery controls
7 | Audio Monitoring & Processing Server
| CPU | Intel Core i9 (12th/13th Gen+) or equivalent Xeon / AMD Ryzen 9
| Cores / Threads | Min. 16 cores / 24 threads
| RAM | 64 GB DDR4 / DDR5 (ECC recommended for stability)
| GPU | NVIDIA RTX 3060 (12GB VRAM) or higher
| System Storage | 1TB NVMe SSD (PCIe Gen3/Gen4)
| Additional Storage (Optional) | 4–8TB HDD for audio archiving
| Network | 2 × Gigabit Ethernet (RJ45)
| Operating System | Ubuntu Server 22.04 LTS or Windows Server 2022
| Power Supply | 750W 80+ Gold PSU
| Chassis | 2U Rackmount or Tower Workstation
| Cooling | High-performance CPU cooling + optimized airflow for GPU
| Redundancy (Optional) | RAID 1 for SSD / redundant PSU
8 | Louroe Digifact A (LE-870) IP audio microphone
| Product Name | Louroe Digifact A
| Model / Part Number | LE-870
| Device Type | Ceiling Mount Digital IP Microphone with Audio Analytics
| Microphone Type | Electret condenser (dynamic audio capture)
| Pickup Pattern | Omnidirectional (one-way audio capture)
| Audio Coverage | Approx. 30 ft (≈ 9.1 m) diameter circle
| Sensitivity | –45 dBV/Pa (1 Pa = 94 dB SPL)
| Frequency Response | 50 Hz – 15 kHz
| Audio Streaming | One-way audio (RTSP compatible)
| Audio Compression | PCM 16-bit, G.711 a-Law & µ-Law, G.726-40, AAC
| Network Interface | 1 × RJ45 (10/100 Mbps) – PoE powered
| Power | PoE IEEE 802.3af (Optional external 5 V DC input)
| Protocols Supported | IPv4, HTTP, RTSP, RTP, TCP, SSH, ONVIF S & T
| Audio Analytics | Built-in analytics (dB threshold, aggression, glass break, car alarm, etc.)
| API | Open API for integration with VMS / third-party software
| Event Actions | TCP notification, external output, pre/post audio recording to NAS
| Memory | 512 MB RAM (typical)
| Environmental | Operating: –20 °C to +50 °C, 10–85% RH
| Dimensions | Ø 119 × 50.8 mm (diameter × height)
| Weight | Approx. 255 g (9 oz)
| Mounting | Ceiling / wall mount (included plate & hardware)
| Certifications | NDAA compliant (in some regions)
| Included Accessories | User manual, 5-pin & 2-pin headers
9 | Ubiquiti UniFi U7 Pro Outdoor Wi-Fi 7 outdoor access point
| Product Name | Ubiquiti UniFi U7 Pro Outdoor
| Device Type | Outdoor Wi-Fi 7 Tri-Band Access Point
| Wi-Fi Standard | Wi-Fi 7 (802.11be), backward compatible with 802.11a/b/g/n/ac/ax
| Frequency Bands | 2.4 GHz, 5 GHz, 6 GHz
| Spatial Streams | 6 (2×2 MU-MIMO each band)
| Total Throughput | ~10.7–10.8 Gbps aggregated
| Max Data Rates | 6 GHz: ~5.7–5.8 Gbps
5 GHz: ~4.3–8.6 Gbps
2.4 GHz: ~688 Mbps
| Antenna Gain | Internal directional:
• 2.4 GHz: ~8 dBi
• 5 GHz: ~11 dBi
• 6 GHz: ~10 dBi
| External Antennas | Omni antennas included (varies by region)
| MU-MIMO | DL/UL MU-MIMO on all bands
| Coverage | ~465 m² (≈ 5 000 ft²) in open space
| Max Clients | 300+ simultaneous clients
| Ethernet Interface | 1 × 1/2.5 GbE RJ45 (PoE+)
| Power | PoE+ (802.3at), 42.5–57 V DC
| Power Consumption | ~21 W maximum
| Weatherproofing | IPX6; IP67 with cable-gland door kit included
| Operating Temp. | –30 °C to +60 °C
| Operating Humidity | 5 % – 95 % non-condensing
| Dimensions | Without mount: 170 × 208 × 66.5 mm
With mount: 170 × 208 × 121.8 mm
| Weight | ~1.2 kg (device only); ~1.33 kg with mount
| Enclosure Material | UV-stabilized polycarbonate & aluminum alloy
| Mounting Options | Wall or pole mount (included)
| Management | Managed via UniFi Network Controller / App
| Advanced Features | Fast roaming, band steering, meshing, RADIUS/VLAN support, guest portal, Wi-Fi schedules
10 | FortiGate 100F next-generation firewall
| Model | FortiGate 100F (FG-100F)
| Form Factor | 1U Rackmount
| Firewall Throughput | Up to ~20 Gbps (1518-byte UDP)
| IPS Throughput | ~2.6 Gbps
| NGFW Throughput | ~1.6 Gbps
| Threat Protection | ~1 Gbps
| IPsec VPN Throughput | ~11.5 Gbps
| SSL-VPN Throughput | ~750 Mbps
| Concurrent Sessions (TCP) | ~1,500,000
| New Sessions/s (TCP) | ~56,000
| Firewall Policies | 10000
| Virtual Domains (VDOMs) | Default/Max: 10/10
| Interfaces – RJ45 | 12 × GE RJ45 ports
| Interfaces – WAN/DMZ/MGMT/HA | RJ45: 2 × WAN, 1 × DMZ, 1 × Mgmt, 2 × HA
| SFP / SFP+ Slots | 4 × GE SFP + 2 × 10 GE SFP+ FortiLink
| USB Port | 1 × USB
| Console Port | 1 × RJ45
| Power Supply | Dual internal AC (100–240 V) / redundant non-hot-swappable
| Power Consumption | ~26.5 W – 29.5 W
| Heat Dissipation | ~100.6 BTU/h
| Operating Temp. | 0 °C – 40 °C
| Storage Temp. | –35 °C – 70 °C
| Humidity | 10 % – 90 % non-condensing
| Dimensions (HxWxD) | 44 × 432 × 254 mm
| Weight | ~3.29 kg
| Max FortiAPs Supported | Up to 128 (total) / 64 (tunnel mode)
| Max FortiClients Registered | ~600 devices
| High Availability | Active/Active, Active/Passive, Clustering
| Security Features | NGFW, IPS, SSL Inspection, Application Control, Anti-Malware, SD-WAN, ZTNA, Threat Intelligence
11 | Ubiquiti UniFi Switch Pro Aggregation (high-capacity aggregation switch)
| Model | USW-Pro-Aggregation
| Device Type | Managed Layer-3 Aggregation Switch
| Ports | 28 × 1/10 Gbps SFP+
4 × 1/10/25 Gbps SFP28
| Total Non-Blocking Throughput | 380 Gbps
| Switching Capacity | 760 Gbps
| Forwarding Rate | 565.44 Mpps
| Layer Features | Static routing, inter-VLAN routing, DHCP server
| Management Interface | In-band Ethernet + UniFi Network Controller / App
| Touchscreen Display | 1.3″ AR LCM color touchscreen
| Power Supply | Internal AC/DC 100–240 V
| Max Power Consumption | ~100 W
| PoE Support | No PoE output (fiber/DAC connectivity only)
| Enclosure | 1U rack-mountable steel chassis
| Dimensions (WxDxH) | 442 × 325 × 44 mm
| Weight | ~4.6 kg (4.7 kg with mounting brackets)
| Environmental (Operating) | –5 °C to +40 °C, 10–90% non-condensing
| ESD/EMP Protection | Air: ±16 kV; Contact: ±12 kV
| Certifications | CE, FCC, IC
12 | Ubiquiti UniFi Switch Pro Aggregation (high-capacity aggregation switch)
| Model | FortiSwitch 148F
| Device Type | Managed Layer-2/L2+ Ethernet Switch
| Form Factor | 1 RU Rack-mount
| Total Ports | 48 × GE RJ45 + 4 × 10GE SFP+ uplinks
| Console Port | 1 × RJ45
| PoE Support | None (0 PoE ports)
| Switching Capacity (duplex) | 176 Gbps
| Max Packets Forwarding | 260 Mpps (million packets per second)
| MAC Address Table Size | 32 K entries
| Network Latency | < 1 µs
| VLAN Support | Up to 4 K VLANs
| Link Aggregation | LAG size up to 8 / up to 128 groups
| Packet Buffer | 2 MB
| DRAM Memory | 512 MB DDR3
| Flash Memory | 64 MB
| ACL Entries | ~640‒768 (varies by datasheet)
| Spanning Tree Instances | 16 – 32 supports (varies)
| Management | FortiLink (via FortiGate), GUI, CLI, SNMP, API
| Layer-2 Features | VLAN, STP/RSTP/MSTP, LACP, IGMP Snooping, 802.1x, Port Mirroring
| Layer-3 Lite | Static routing & basic L3 functions (varies by firmware)
| Power Supply | Internal AC 100–240 V
| Typical Power Consumption | ~55.8 W / Max ~57 W
| Dimensions (H×D×W) | 44 × 260 × 440 mm
| Weight | ~3.46 kg
| Operating Temp. | 0 – 45 °C (32 – 113 °F)
| Humidity | 10 % – 90 % non-condensing
| Airflow | Side-to-back
| Certifications | CE, FCC, UL, RoHS2
13 | Ubiquiti UniFi Switch Pro 24 PoE (USW-Pro-24-PoE)
| Model | USW-Pro-24-PoE
| Device Type | Managed PoE Ethernet Switch
| Form Factor | 1U Rackmount / Desktop
| Total Ports | 24 × Gigabit RJ45
| PoE Ports | 24 × PoE+ (802.3af/at), up to 30 W per port
| Uplink Ports | 2 × 10 Gbps SFP+/RJ45 (combo)
| Aggregate PoE Budget | 400 W (typical)
| Switching Capacity | 128 Gbps
| Forwarding Rate | ~95.24 Mpps
| Layer | Layer 2 with Layer 3 Lite features
| VLAN Support | Yes (802.1Q)
| Link Aggregation | LACP supported
| Management | UniFi Network Controller / UniFi App
| Touchscreen Display | Yes (front LCD touchscreen)
| PoE Modes Supported | 802.3af, 802.3at
| Max PoE Per Port | 30 W
| PoE Power Management | Per-port priority & scheduling
| L2 Features | STP/RSTP/MSTP, IGMP Snooping, QoS
| Layer 3 Features | Static routing, DHCP server
| Network Protection | IPv4/IPv6 ACLs
| Environmental (Operating) | 0–40 °C, 10–90 % non-condensing
| Power Supply | Internal AC 100–240 V
| Power Consumption | ~450 W (max under PoE load)
| Dimensions (W×D×H) | ~442 × 257 × 44 mm
| Weight | ~4.5 kg
| Mounting Options | Rack, Wall, Desktop
| Certifications | CE, FCC, IC
14 | APC Smart‑UPS Ultra On‑Line series of high-performance uninterruptible power supplies (UPS)
| UPS Topology | Double-conversion On-Line (true online UPS) with pure sine wave output
| Input Voltage Range | ~187 – 275 V AC (model dependent)
| Input Frequency | 40 – 70 Hz auto-sense
| Output Power Capacity | Range from ~2200 VA/2200 W up to ~8000 VA/8000 W (specific by SKU)
| Nominal Output Voltage | 220/230/240 V AC (region dependent)
| Output Waveform | Pure sine wave (ideal for servers & sensitive electronics)
| Crest Factor | 3:01
| Output Frequency | 50/60 Hz ± 3 Hz sync to mains
| Efficiency (Green Mode) | Up to ~98.5 % (where supported)
| Battery Technology | Lithium-ion (Li-Ion) – long life and high energy density
| Battery Runtime (Typical) | ~5 min at full load (5000 W model); longer at lower loads; expandable with external battery packs
| Battery Life Expectancy | ~8–10+ years
| Recharge Time | ~1.5 hours to full recharge
| Outlets / Connections | IEC 320 C13 & C19 outlets (varies by model) up to 10 on some units
| Management / Communication Ports | USB, Ethernet SmartConnect, network management card embedded (varies)
| Display | Auto-rotating high-resolution LCD panel
| Form Factor | Rackmount / Tower convertible; typical size 1U–4U depending on capacity
| Protection Features | Internal bypass, surge protection, EPO support
| Operating Temp. | ~0 – 40 °C
| Operating Humidity | ~0 – 95 % non-condensing
| Certifications | CE, RoHS, IEC/EN 62040 standards
15 | Yeastar S-412 VoIP PBX
| Model | Yeastar S-412 VoIP PBX
| System Type | Hybrid analog + VoIP PBX (small business)
| User Capacity | Up to 20 internal users (mixed analog & VoIP)
| Concurrent Calls | Up to 8 simultaneous calls
| VoIP Trunks | 4 SIP trunks
| Fixed Ports | 8 × FXS RJ11 built-in
| Max FXS Ports | Up to 12 (with modules)
| Customizable Ports | Up to 4 FXO/BRI (external lines)
| Cellular Ports | Up to 2 GSM/3G/4G channels (one data 4G)
| LAN / WAN | 1 × 10/100 Mbps LAN, 1 × 10/100 Mbps WAN
| Network Protocols | SIP (RFC3261), IAX2
| Transport Protocols | UDP, TCP, TLS, SRTP
| Supported Codecs | G.711 (a/u-law), G.722, G.726, G.729A, GSM, Speex, ADPCM, iLBC, H.263/H.264, MPEG4
| DTMF Support | In-band, RFC4733, RFC2833, SIP INFO
| Fax Support | T.30 & T.38; Fax-to-Email
| Storage / Media | TF card slot for recording/storage
| Built-in Features | IVR, Auto provisioning, Voicemail, Call recording, Queues, Conferencing, LDAP server, Email/SMS alerts, CDR/Billing, CRM/Hotel/Apps support
| Linkus UC Support | Yes – mobile/desktop unified comms client
| Remote Management | Secure remote monitoring/management tool
| Power Supply | 12 V DC, 3.33 A (approx.)
| Power Consumption | ~9.0 – 25.6 W
| Dimensions | ~290 × 180 × 33 mm
| Weight | ~0.68 kg
| Operating Temp. | 0 – 40 °C
| Humidity | 10 – 90 % non-condensing
| Mounting | Desktop & wall mount
| Installation | Plug-and-play setup with intuitive web GUI
| Security | Built-in firewall, TLS/SRTP encrypted signalling/audio
16 | INIM Previdia UltraVox — an integrated fire detection + voice evacuation (EVAC) + public address system
| Product Type | Integrated fire detection & EVAC control panel
| Model / Series | Previdia UltraVox
| Standards / Certifications | EN54-2 (control panel), EN54-4 (power supply), EN54-16 (voice alarm EVAC), EN54-21 (networked systems), EN12094-1 (gas extinguishing interfaces)
| Architecture | Modular (expandable up to 4 cabinets, up to 32 IFM/IFAM modules)
| Integrated Functions | Fire detection, alarm, voice evacuation (EVAC), public address (PA), audio entertainment
| Base Modules Included | FPMCPU control unit, FPAMIAS EVAC control, IFAMPSU power supply 1000 W, IFAMEVAC audio matrix, IFAMAMP 250 W amplifier, IFM2L loop module, PTT microphone
| Power Supply Voltage | 90 – 264 VAC, 47 – 63 Hz
| Maximum Current Draw | 8.5 A @ 115 VAC; 5 A @ 230 VAC
| DC Output Voltage | 26 V DC nominal (20 – 27.6 V)
| Speaker Line Output Voltage | 100 Vrms
| Maximum Power per PSU Module | 1000 W (expandable to 4000 W with 4 cabinets)
| Max Current from PSU Module | 38 A (35 A available to system)
| Battery Support | 2 × 12 V batteries (17 Ah or 38 Ah)
| Speaker Line Supervision | 20 kHz pilot tone (no EOL needed above 20 W)
| Network Interfaces | IDANET (Ethernet or fiber), optional Hornet+ RS485 or TCP/IP connection
| Audio Zones Supported | Up to ~1000 audio zones (system capable when expanded)
| Audio Sources / Control | 8 local digital audio tracks + 8 network digital audio tracks
| Analog Audio Inputs | 2 × analog music inputs + 2 × AUX inputs with priority detection
| Amplifier Support | Up to ~30 × Class-D 250 W amplifiers in network
| Display | Dual 7″ color touchscreen displays (65,000 colours)
| Cabinet / Enclosure | PRCAB+ modular cabinet (IP30)
| Protection / IP Rating | IP30
| Operating Temperature | −5 °C .. +40 °C
| Dimensions | 675 × 430 × 260 mm (per cabinet)
| Weight | ~23 kg (without batteries)
| Color Options | RAL7042 (grey) or RAL3001 (red)
| Event / Log Capability | Stores recent fire & EVAC events (typically thousands)
| Expansion / Networking | Up to 48 control panels via IDANET, shared audio across network
17 | INIM ED100 – Addressable Optical Smoke Detector (EN54-7)
| Model | ED100
| Product Type | Addressable optical (photoelectric) smoke detector
| Standard Compliance | EN54-7 / EN54-17 (with isolator) compatible
| Sensor Type | Optical chamber using scattered light (Tyndall effect)
| Power Supply | 19 – 30 V DC
| Current Draw (Standby) | ~200 µA
| Current Draw (Alarm) | ~10 mA @ 27.6 V
| Output Contact (Isolator) | Max 14 mA (internally limited)
| Sensitivity Settings | Adjustable: 0.08, 0.10, 0.12 (default), 0.15 dB/m
| Addressing | Manual address selection (1–240)
| Operating Temp. | –5 °C to +40 °C
| Humidity (non-condensing) | Up to 95 % RH
| Dimensions (Ø × H) | 110 mm × 46 mm (with base)
| Weight | ~160 g (with base); ~90 g (without base)
| Mounting | Compatible base (e.g., EB0010) for addressable loop
| Loop Connectivity | 2-wire twisted/shielded between fire panel and detector
18 | INIM IL0010 remote alarm indicator — a visual LED repeater used in fire alarm systems
| Model | IL0010
| Type | Remote LED indicator (alarm visual repeater)
| Purpose | Replicates detector alarm signals visually at a remote location
| Compatible With | Addressable detectors (ENEA series) and conventional detectors (IRIS series)
| Power Supply | 19‒30 V DC
| Current Consumption (Alarm) | ~20 mA @ 27.6 V DC
| Signal Type | LED optical flash indicator (visual alarm)
| Housing Material | ABS plastic
| Protection Rating | IP42 (indoor use protection)
| Operating Temperature | –5 °C to +40 °C
| Humidity (non-condensing) | Up to 95 % RH
| Dimensions (W×H×D) | ~79 × 76 × 27 mm
| Weight | ~45 g
| Mounting | Wall or ceiling mount near detector location
| Certifications | CE declaration of conformity (EU)
19 | INIM ES0020RE – Addressable Loop-Powered Siren with Flash
| Model | ES0020RE
| Device Type | Addressable loop-powered siren + strobe (audible/visual indicator)
| Protocol | Enea / Inim addressable fire alarm loop
| Power Supply (Loop Powered) | 17 – 60 V DC
| Current Consumption | 4 – 41 mA (depending on tone selected)
| Beacon Current | ~5 mA (visual flash)
| Sound Output (at 1 m) | Up to ~106 dB(A) (adjustable based on tone)
| Tones | 32 selectable tones (via DIP switch or programming)
| Protocol Module Included | EU311S (loop isolator module included)
| Protection Rating | IP65 / IP67 (weatherproof – suitable for outdoor use)
| Operating Temperature | −25 °C to +70 °C
| Color | Red housing
| Certifications | EN54-3 (audible alarm), EN54-17/18 (loop & visual where applicable)
| Mounting | Direct installation on fire alarm loop with supplied base
| Typical Dimensions (approx.) | Ø ~98 mm × height ~104 mm
| Weight (approx.) | ~250 g