Annex 5.  Technical Specifications for smart meters and communication modules

|  | Total |  |  |
| --- | --- | --- | --- |
|  | 1 phase | 3 phase direct connection | 3 phase TC Connection |
| Total Meters | 3 | 11 | 0 |

| TECHINCAL SPECIFICATIONS SMART METERS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase | Smart meters, three-phase direct connected |  |  |  |  | Smart meters, three-phase transformer connected |  |  |  |
| Accuracy class: for Active Energy for Reactive Energy | B 2 | B 2 |  |  |  |  | С 2 |  |  |  |
| Reference current | min. 5 A | min. 5 A |  |  |  |  | min. 5 A |  |  |  |
| Maximum current, Iref | min. 60 A | min. 80 A |  |  |  |  | min 5 A |  |  |  |
| Minimum current | 0.05 Iref for active / 0.05 Iref for reactive | 0.05 Iref for active / 0.05 Iref for reactive |  |  |  |  | 0.01 Iref for active / 0.02 Iref for reactive |  |  |  |
| Reference voltage, Un | 230 V | 3×230/400 V |  |  |  |  | 3×230/400 V |  |  |  |
| Reference frequency | 50 Hz (± 2 %) | 50 Hz (± 2 %) |  |  |  |  | 50 Hz (± 2 %) |  |  |  |
| Inherent consumption (EN 50470-3 , IEC 62053/21-22-23, IEC 62053-61, without communications overhead) of current circuit, not more than of voltage circuit, not more than | 1 VA 2 W / 10 VA | 1 VA 2 W / 10 VA per phase |  |  |  |  | 1 VA 2 W / 10 VA per phase |  |  |  |
| Inherent consumption of voltage circuit (IEC 62052-11, IEC 62053/21-22-23, IEC 62053-61, including communication overhead), not more than | 5 W / 10 VA | 3 W / 10 VA per phase |  |  |  |  | 3 W / 10 VA per phase |  |  |  |
| Internal clock accuracy (IEC 62052-21) | ≤ 0.5 s / 24 h | ≤ 0.5 s / 24 h |  |  |  |  | ≤ 0.5 s / 24 h |  |  |  |
| Insulation strength (IEC 61010-1-90) | 4 kV, 50 Hz, 1 min | 4 kV, 50 Hz, 1 min |  |  |  |  | 4 kV, 50 Hz, 1 min |  |  |  |
| Shock voltage (IEC 60060-1) | 6 kV, 1.2/50 μs | 6 kV, 1.2/50 μs |  |  |  |  | 6 kV, 1.2/50 μs |  |  |  |
| Electrostatic discharge (IEC 61000-4-2) | 15 kV | 15 kV |  |  |  |  | 15 kV |  |  |  |
| High frequency radiant field (IEC 61000-4-3) | ≥ 30 V/m | ≥ 30 V/m |  |  |  |  | ≥ 30 V/m |  |  |  |
| High frequency interferences (IEC 6100-4-4) | 4 kV | 4 kV |  |  |  |  | 4 kV |  |  |  |
| Surge immunity test (IEC 6100-4-5) | 6 kV | 6 kV |  |  |  |  | 6 kV |  |  |  |
| IP rating | IP54 | IP54 |  |  |  |  | IP54 |  |  |  |
| Mechanical class | min. M1 | min. M1 |  |  |  |  | min. M1 |  |  |  |
| MTL (Mean Total Lifetime) | not less 15 years | not less 15 years |  |  |  |  | not less 15 years |  |  |  |
| MTBF (Mean Time Before Fail) | less than / year 0.5% | less than / year 0.5% |  |  |  |  | less than / year 0.5% |  |  |  |
| CERTIFICATES | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase |  |  |  |  | Smart meters, three-phase direct connected |  |  |  | Smart meters, three-phase transformer connected |
| MID certificate | Should be issued by European recognized lab |  |  |  |  |  |  |  |  |  |
| PLC certificate | PLC PRIME 1.3.6 and 1.4 |  |  |  |  |  |  |  |  |  |
| Production certificate | According to MID (mode D) |  |  |  |  |  |  |  |  |  |
| ISO | 9001 |  |  |  |  |  |  |  |  |  |
| FUNCTIONAL SPECIFICATIONS - METERING PARAMETERS | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase |  |  |  |  | Smart meters, three-phase direct connected |  |  | Smart meters, three-phase transformer connected |  |
| METERING DATA | - Actual meter readings; - Periodic (billing) meter readings: Day, month; - Interval meter readings: 15’, 30’, 60'; day - Timestamp. |  |  |  |  |  |  |  |  |  |
| MULTI-RATE METERING | - Up to 4 tariff registers, flexible adjustment of tariff intervals; - Min. 4 changeovers per day; - Tariff indicator is displayed on LCD and transmitted to an external system; - Active and passive tariff plans, configurable activation time of the passive tariff plan. |  |  |  |  |  |  |  |  |  |
| MEASURED VALUES | - Active energy, class B, export/import; - Reactive energy, class 2, 4 quadrants; - Apparent energy; - Active/reactive power, apparent power; - Phase voltage/current, instantaneous value (True RMS, integration period 1 s); - Voltage angle values relative to the voltage in first phase and phase currents relative to relevant phase voltages. |  |  |  |  |  |  |  |  |  |
| METERING CALENDAR | - Up to 4 seasons per year; - Up to 7 daily profiles per week; - Up to 30 special days per year; - Support of movable holidays. |  |  |  |  |  |  |  |  |  |
| DATA STORAGE | - Non-volatile memory; - Not less than 3 interval profiles and 1 billing profile. - Storage capacity: - 15 minutes interval profile: not less than 45 days for 6 parameters - Asynchronous profile (spontaneous events), last entries data. |  |  |  |  |  |  |  |  |  |
| OPERATING MODES | - Normal mode; - Energy saving mode - real time clock, opening sensors, and data displaying are active. |  |  |  |  |  |  |  |  |  |
| POWER QUALITY CONTROL | - Quality indexes: - average voltage; - voltage sags and swells; - outages; - network frequency; - THD for voltage/current harmonics; - Remote or local configuring of parameters thresholds and control actions. |  |  |  |  |  |  |  |  |  |
| FUNCTIONAL SPECIFICATIONS - MANAGEMENT AND CONTROL PARAMETERS | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase | Smart meters, three-phase direct connected |  |  |  |  | Smart meters, three-phase transformer connected |  |  |  |
| DLMS/COSEM SUPPORT | - IEC 62056 compliant; - Object Identification System compliant; - Standard data models; - Standard communications protocols. |  |  |  |  |  |  |  |  |  |
| DATA TRANSMISSION | - On demand; - By Schedule; - Remote HES request; - Local request (via optical port). - Internal interface for transformer connected meters (which is an integrated part of the data concentrator) |  |  |  |  |  |  |  |  |  |
| SOFTWARE UPGRADE | - Remote (via communication channel); - Local (via RS-485 or optical port) |  |  |  |  |  |  |  |  |  |
| FRAUD AND THEFT PROTECTION | - Non-stop monitoring, including sleep mode time; - Meter cover opening sensor; - Terminal block cover sensor; - Reverse meter connection control; - Strong magnetic field detection; - Events registering in relevant logs; |  |  |  |  |  |  |  |  |  |
| BUILT IN CLOCK | - Real-time clock with 0.5 s accuracy per day; - IEC 62052-21 standard compliant; - External synchronization with HES |  |  |  |  |  |  |  |  |  |
| EVENTS AND ALARMS HANDLING | - Continuous control of current state of meter functional nodes and alarms/events; - Standard set of events processing including: registration in special logs and registers, event report sending, states displaying; - Different types of event logs; - Asynchronous sending of Event; - Notification can be configured for specific events. |  |  |  |  |  |  |  |  |  |
| METER SELF CONTROL | - Built-in test for continuous self-control; - Quick response on severe error |  |  |  |  |  |  |  |  |  |
| POWER LOAD CONTROL | - Basic relay (80 A) – for direct connected meters only - Control modes: - remote (by command) - local (by condition) - manual - by push button - Basic relay status displayed on the meter LCD |  |  |  |  |  |  |  |  |  |
| METER PARAMETRIZATION | - Remote (via communication channel) or local (via optical port); - Access rights assignment from HES; |  |  |  |  |  |  |  |  |  |
| THRESHOLDS MANAGEMENT | - Threshold for active power, active power demand, current/voltage (per phase), differential current (direct connected meters only); - Remote or local configuring of parameters thresholds; - Possibility to disconnect consumer from the network, when a threshold is crossed. |  |  |  |  |  |  |  |  |  |
| BACK-UP POWER SUPPLY | - Supports clock/meter operation when the power is off; - Battery, lifetime - not less than 10 years. |  |  |  |  |  |  |  |  |  |
| FUNCTIONAL SPECIFICATIONS - SECURITY | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase |  | Smart meters, three-phase direct connected |  |  |  |  | Smart meters, three-phase transformer connected |  |  |
| INFORMATION SECURITY | - Communication encryption (AES-GCM-128 security suite); - Data access according to access rights stated; - Firmware protection. |  |  |  |  |  |  |  |  |  |
| FUNCTIONAL SPECIFICATIONS - INTERFACES | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase |  |  | Smart meters, three-phase direct connected |  |  | Smart meters, three-phase transformer connected |  |  |  |
| OPTICAL PORT | - IEC 62056-21 Compliant; - Data rates - up to 19200 bps; - Password protected; - Multiple access levels. |  |  |  |  |  |  |  |  |  |
| BUILT-IN DISPLAY | - LCD with min 8 lines; - Configurable decimal places (up to 3 digits); - Manual and automatic scrolling; - Backlight. |  |  |  |  |  |  |  |  |  |
| TEST OUTPUTS | - 2 led outputs; - Active and reactive energy; |  |  |  |  |  |  |  |  |  |
| PUSH BUTTON | - Scroll meter screens; - View data on LCD, when the power is off. |  |  |  |  |  |  |  |  |  |
| RS485 SERIAL INTERFACE | - EIA/TIA-485A standard; - Baud rate - up to 38400 bps |  |  |  |  |  |  |  |  |  |
| FUNCTIONAL SPECIFICATIONS - REMOTE COMMUNICATION | REQUIRED SPECIFICATIONS |  |  |  |  |  |  |  |  |  |
| Specifications | Smart meters, single-phase |  |  |  | Smart meters, three-phase direct connected |  | Smart meters, three-phase transformer connected |  |  |  |
| POWER LINE COMMUNICATION (PLC) | - OFDM PLC Module; - PRIME compliant with specification ITU-T G.9904 - CENELEC and FCC bands - Auto-discovery; - Repeating. |  |  |  |  |  |  |  |  |  |
| REMOTE DISCONNECTION | - Bi-stable switching module for local or remote disconnection/reconnection; - Min. 10 000 mechanical disconnections/reconnections under maximum load. |  |  |  |  |  |  |  |  |  |

| TECHNICAL SPECIFICATIONS communication modules |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Specifications | Smart meters, single-phase | Smart meters, three-phase |  |  |  |  |
| Compatibility | Compatible with chosen meter |  |  |  |  |  |
| 3GPP Interface | - 2G/3G/4G (one of them or several) - SIM or eSIM; - Built-in protocol stack: TCP/IP, UDP/IP - IPv4/IPv6 support - Direct communication upstream with the head-end system; - Data transmission by schedule or on request from the head-end system; - Connector for external antennas. |  |  |  |  |  |
| Interfaces | - min. 1 x RS-485 or RS-232 for connection of meter with communication module - Cellular 2G/3G/4G auto |  |  |  |  |  |
| Design | - Installation under sealable meter terminal cover, to prevent unauthorised access - Housing made of non-flammable material - Power supply from the meter |  |  |  |  |  |
| Additional equipment to be supplied | Compatible external antennas for each module |  |  |  |  |  |